## Setup
Enter Stakeholder Group Name in cell A2:
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Fuel Requirements for Black Start Resources

## 1. Interest Identification
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OC Interest Identification
1 | Sufficient black start capabilities be available regardless of situation
2 | Improve fuel assurance for black start resources
3 | Support all fuel type eligibility for black start resources
4 | Avoid creating stringent requirements that eliminate existing black start resources
5 | Clearly define performance standards for operating hours during a restoration event for each fuel type
6 | Clearly define testing requirements related to fuel security
7 | Explore options for fuel assurance/storage requirements
8 | Determine if fuel requirements for black start resources have to be defined in the Manuals and/or the OATT
9 | In the transiton or implementation phase for existing units, include an RFP type procurement process.
10 | Ensure storage resources are included in proper compliance with order 841.
11 | Ensure cost effective application of Black Start resources
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OPTIONS MATRIX
Solution Options
# | Design Components | Priority | Status Quo | A | B | C | D | E | F
A | Zonal Level of Fuel Assurance for Black Start resources |  | N/A | All Black Start resources allocated to a TO zone must be fuel assured. | Determine the number of Black Start resources that have to be fuel assured allocated to each TO zone based on an analysis. | X% of Black Start resources allocated to a TO zone must be fuel assured. | Minimum of two Black Start resources allocated to the TO zone at separate sites must be fuel assured. Determine the Black Start resources that have to be fuel assured based on an analysis.
1 | Minimum Level of Fuel Assurance for Black Start Resources |  | N/A | Minimum of one individual Fuel Assured Black Start (meeting the requirements in Design Component Section B and C) resource per zone. If an individual Fuel Assured Black Start resource is not currently available, two Black Start resources connected to different interstate gas pipelines is an acceptable alternative to meet the minimum.
2 | Additional Fuel Assurance Criteria Beyond Minimum |  | N/A | Any site identified by zonal reliability analysis that causes an incremental restoration time increase of 10 hours or more
B | Universal Black Start Requirements
1 | Duration / Run Hour requirements | High | 16 hours per black start resource (even if resources on the same site share a common fuel source) | 16+ Hours per black start resource | 24 Hours per black start resource
2 | Emissions Permit Limitations | Medium | Different states and Black Start resources have various limitations for emission waivers. PJM currently does not track. | Requirements for the Black Start resources to obtain emission permit waivers to accommodate operations during a restoration situation (operating below normal economic min values), if required. | No requirement but higher weighting will be applied during the Black Start RFP process to resources with emission permit waivers. | PJM will provide education and awareness to states and coordinate/develop waiver process. PJM will create a template for emission waivers. | Requirements for the fuel assured Black Start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required.
3 | Non-Fuel Consumables (e.g.. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement.
4 | Bilateral Compensated Black Start Unit Requirements |  | NERC Requirements | Must meet all fuel assurance requirements to be considered a fuel assured Black Start resource. Must enter PJM Black Start service through RFP process.
5 | Starting System Requirements |  | N/A | Capability to provide 3 starts with a minimum 16 hours idle time
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Limitations based on the number of resources within the same pipeline segment | Not allowed to be a fuel assured Black Start without on-site fuel capability. | non-fuel assured Black Start must have firm gas transport | Dual fueled units capable of starting solely on on-site fuel | Gas only units connected to multiple interstate gas pipelines | Gas only unit connected to a single gas source fed directly from a gas supply basin / gathering system ahead of interstate pipelines
2 | Oil | High | 16 hours of run hour requirements | Sufficient oil storage on-site at all times for each Black Start resource in a site to meet minimum run time requirements (if resources shares the same fuel source) | Firm refueling contracts | Firm oil pipeline connections
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Analysis with X % of confidence of most restrictive seasonal flow to support the assigned Black Start MW. | Performance verification will be based on the most limiting season of the past X years of performance history. | Single site simultaneous verification test | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM | Calculate black start MW quantities for each month of the year to account for seasonality
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | The pond level must be maintained to satisfy run hour requirements to meet the Black Start commitment. | Pond level must be maintained to satisfy run hour requirements and telemetry. | Use the 24 Hour Capacity factor rather than ICAP. If wish to use as non-assured fuel resources, then use the traditional ICAP value and have a 16 hour run requirement.
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | Stored energy must always be kept on-site for each Black Start resource to meet minimum run time requirements | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM and meet all requirements in Design Component Section B and PJM OATT Schedule 6A
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | A combination of on-site fuel inventory, water level, stored energy, etc. must always be kept on-site for each Black Start resource to meet minimum run time requirements | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM and meet all requirements in Design Component Section B and PJM OATT Schedule 6A | Calculate black start MW quantities for each month of the year to account for seasonality
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Analysis with X % of confidence of most restrictive season to support the assigned Black Start MW. |  |  | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM and meet all requirements in Design Component Section B and PJM OATT Schedule 6A | Calculate black start MW quantities for each month of the year to account for seasonality
8 | DER/DR with on-site generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Not allowed to be a fuel assured Black Start resource without on-site fuel capability able to meet the minimum run requirements |  | Meet all requirements in Design Component Section B and PJM OATT Schedule 6A
D | Fuel Assurance Testing & Verification Requirements (for Fuel Assured Resources Only)
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel on alternate years
2 | Concurrent fuel testing | High | None | All Black Start resources connected to the same fuel source test concurrently
3 | Online fuel transition testing | Medium | None | One test per year to demonstrate the ability to switch between fuels. | Provide data on fuel switching restrictions/limitations that unit may have.
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Fuel verification at least at X frequency or upon PJM request | Telemetry of fuel inventory | Black start units report to PJM dispatch and units are placed in max-emergency when they carry fuel less than the minimum run hour requirement | Fuel verification on Black Start test forms. | Based on resource unit and fuel type, on-site fuel inventory, water level, stored energy, etc. must be confirmed to PJM on a monthly basis via eDART or telemetry if preferred. | For natural gas resources, PJM will validate all contractual arrangements for gas supply/delivery.
5 | Starting Systems verification |  | n/a | Starting system limitations must be communicated as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if starting systems not able to meet the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately.
6 | Non-Fuel Consumables (e.g.. water, ammonia) inventory verification |  | n/a | Non-fuel consumables inventory limitations must be communicated as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if consumables fall below the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately.
7 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability must take into account unit limitations i.e. Steam bypass, if applicable | Either the unit's ICAP or the PJM determined MW with 90% confidence is used for unit compensation
8 | Black start MW capability verification | High | The annual capacity test | All Black Start resources connected to the same fuel source test concurrently
9 | Emission permit limitation verification |  | None | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable.
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours | Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance. | Develop a methodology to determine which portion of the incremental capital costs are solely necessary for Black Start fuel assurance. | PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for Black Start by netting energy revenues that are a direct result of the capital expenditures during the capital recovery period
1 | Fuel Assurance Compensation Capital Recovery Period. |  |  | The greater of the schedule 6A recovery period based on the age of the unit or 10 years.
2 | Portion of fuel assured capital recovery that is solely necessary for Black Start |  | N/A | In order to determine how much of the capital recovery is solely necessary for Black Start, any energy revenues obtained as a result of a fuel assurance conversion, by month, would be netted from the black start revenues for that month.
2 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG Black Start resources are compensated for carrying cost of the full MTSL volume. For Black Start resource that share tanks only one resource gets compensated. | Oil , propane and LNG tanks shared between resources will proportionally share compensation of the MTSL value. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL.
3 | Onsite fuel, water level, stored energy, etc. compensation | Medium | None | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM dispatch must be notified within 24 hours. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. If the fuel inventory, water level, stored energy falls below the run hour requirement as the result of a regulatory requirement for approved planned outage (full derate), monthly Black Start revenues will not be withheld. | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. | Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy, or non-fuel consumables falls below the run hour requirement as the result of a regulatory requirement for an approved planned outage (full derate) or restoration events, monthly Black Start revenues will not be withheld. If fuel inventories fall below 16 hrs due to PAI event, monthly Black Start revenues will be foregone.
4 | Fuel Assurance Testing Compensation |  | None | Units will be compensated for fuel assurance testing on both fuels. | Compensation to be similar to current Black start testing. Compensation for both tests on both fuels for dual fuel units.
5 | Compensation for non-CRF Black Start resources and non Black Start resources that do not require capital projects to provide fuel assured Black Start. |  | Base formula rate | Adder to the base formula rate for fuel assurance. | Increase the fuel storage component of the base formula rate and make available for all resource types in some form. | Increase the Z factor based on the fuel assured resource type.
6 | Run of River Hydro Compensation |  | Base formula rate | Tier 1: 90% Confidence level for 16 hour minimum run requirement. Allocation X factor = 0.02 and Incentive Z factor = 20%. Monthly validation: None. Tier 2: 90% Confidence level for 10 hour minimum run requirement (or as defined by TO restoration plan). Allocation X factor = 0.01 and Incentive Z factor = 10%. Monthly validation: If a 10 hour or greater minimum run requirement is used, a monthly verification will take place to determine if unit(s) could meet assigned MW requirement for 16 hour run time based on average monthly flow. If capable of meeting, Incentive Z factor is increased to 20% for the Month's Base Formula Rate. Units will need to provide one years notice to switch tiers. New units on the Capital Recovery Rate will specify the Tier of service they will provide when they submit their initial proposal. | 90 % confidence level for 10 to 16 hours minimum run requirement. Allocation X factor = 0.01 and incentive factor = 10% | Non-fuel assured run of river black start sites is base formula rate (status quo). Fuel assured run of river black start sites Allocation X factor = 0.02 and Incentive Z factor = 10%. | Calculate black start revenues based on monthly black start quantities for run of river hydro resources
7 | Pumped Storage Hydro Compensation |  | Base formula rate | Same as Run of River | 90 % confidence level for 16 hours minimum run requirement. Allocation X factor = 0.01 and incentive factor = 10%
8 | Energy Storage, Hybrid, Intermittent Resources |  |  | Non-fuel assured black start sites is base formula rate (status quo). Fuel assured black start sites Allocation X factor = 0.02 and Incentive Z factor = 10%. | Calculate black start revenues based on monthly black start quantities for intermittent resources
9 | Cost Allocation |  | Status Quo | system wide allocation or status quo
F | Implementation |  | N/A
1 | Implementation Date |  |  | New business rules would take effect 2023 RTO-Wide RFP and onwards
2 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service Existing Black Start resources that do not clear the RFP may be terminated and if terminated will recover their investment in accordance with Section 6 of Schedule 6A of the OATT | Existing non-fuel assured black start sites can participate in future RFPs with fuel assured proposals
3 | New Black Start resources | High | None | Add the requirement that any submission to a future RFP must meet the fuel assurance requirements. RFP process would not change beyond that. | New black start sites can participate in future RFPs with both fuel assured and non-fuel assured proposals
4 | Procuring additional Black Start resources because of deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Existing incremental RFP process would be used
5 | Reliability Backstop |  | PJM Manual M14D Section 10.3 | Existing Reliability Backstop Process in PJM Manual M14D Section 10.3 to be implemented in the event of insufficient response to RTO wide RFP or future incremental RFP (2 failed RFP processes), to meet minimum of one black start site per zone meeting fuel assurance criteria and reliability (PLUS) criteria beyond minimum criteria for high impact black start sites. For Reliability Backstop RFP, TO required to submit RFP proposal.

## 2a. Design Component Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE/ PROPOSAL MATRIX
Packages
#+A7:E10 | Design Components | Priority | Status Quo | A - removed | B - IMM | C - removed | D - removed | E | F - PJM | G
A | Zonal Level of Fuel Assurance for Black Start resources |  | N/A | All Black Start resources allocated to a TO zone must be fuel assured (Only fuel assured Black Start resources may be used to meet M36 Attachment A requirements) | Fuel Assurance needs to be defined and transparent. | All Black Start resources must be fuel assured. | Each TO zone must have one allocated fuel assured black start resource, on a unit count basis; Additional fuel assured black start resources will only be awarded based on cost / benefit analysis performed by PJM with input from the TO. 1. TO zones shall have a minimum of one allocated fuel assured black start resource on a unit count basis, with any additional allocated fuel assured black start resources to be awarded only on the basis of a cost / benefit analysis performed by PJM with input from the affected TO. 2. For TO zones that already have more than one fuel assured black start resource, existing fuel assured black start resources will not be terminated to be under one fuel assured black start resource for that TO zone. 3. There may be scenarios where existing fuel-assured non-black start resources submit an RFP proposal to enter Black Start Service with only black start conversion costs. In these cases PJM may award fuel assured resources in TO zones that are at or above one fuel assured black start resource per zone as long as no additional fuel assurance capital costs are required. 4. PJM may not award fuel assurance conversions in TO zones where the one fuel assured black start resource per zone requirement by resource count is already met, unless PJM, with assistance from the affected TO, performs engineering and economic assessments to ensure that incremental fuel assured black start resources are likely to result in improved restoration times consistent with a benefits/cost analysis. a. Cost/benefit analysis performed as part of an RFP evaluation process will generally include the following: i. Projected analysis of incremental increase in restoration time greater than XX hours to reflect the additional restoration complexity for alternate black start resources serving initial critical loads via alternate cranking paths. ii. Location / geographic diversity of fuel assured black start resources with respect to gas pipelines iii. Gas pipeline risk assessment as applicable b. PJM, with assistance of the affected TO, will review the cost/benefit analysis results and recommendations with applicable state commissions, aligning with state commission risk tolerance. c. PJM will also provide projected cost summaries for additional fuel assured black start resources as informational updates for the PJM OC and MIC. d. PJM will provide cost/benefit analysis results and projected cost summaries for state commissions and PJM OC/MIC in accordance with CEII and confidentiality processes. | Each TO zone must have one allocated fuel assured black start resource, on a unit count basis; No fuel assurance conversions above the one per zone cap. 1. TO zones shall have one allocated fuel assured black start resource, on a unit count basis; PJM will not award additional fuel assurance conversions if the minimum of one fuel assured black start resource is already met. 2. For TO zones that already have more than one allocated fuel assured black start resource, existing fuel assured black start resources will not be terminated to be under the one fuel assured black start resource per zone cap. 3. There may be scenarios where existing fuel-assured non-black start resources submit an RFP proposal to enter Black Start Service with only black start conversion costs. In these cases PJM may award fuel assured resources in TO zones that are at or above one fuel assured black start resource per zone as long as no additional fuel assurance capital costs are required.
1 | Minimum Level of Fuel Assurance for Black Start Resources |  | N/A |  | Criteria need to be defined. |  |  |  | Minimum of one individual Fuel Assured Black Start (meeting the requirements in Design Component Section B and C) resource per zone. If an individual Fuel Assured Black Start resource is not currently available, two Black Start resources connected to different interstate gas pipelines is an acceptable alternative to meet the minimum. | Same as PJM
2 | Additional Fuel Assurance Criteria Beyond Minimum |  | N/A |  | Criteria need to be defined |  |  |  | Any site identified by zonal reliability analysis that causes an incremental restoration time increase of 10 hours or more | Same as PJM
B | Universal Black Start Requirements
1 | Duration / Run Hour requirements | High | 16 hours per black start resource (even if resources on the same site share a common fuel source) | 16 hours or as defined in hydro proposal per black start resource (even if resources on the same site share a common fuel source). | 16 Hours | 24 hours per black start resource (even if resources on the same site share a common fuel source) | Same as PJM | Same as PJM | 16+ Hours per black start resource | Same as PJM
2 | Emissions Permit Limitations | Medium | Different states and Black Start resources have various limitations on operations of Black Start resources. PJM currently does not track. | Requirements for the Black Start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required. | Applicable permit limits need to tracked. Waivers should be required to accommodate operations during a restoration situation. | Same as PJM | Same as PJM | Same as PJM | Requirements for the Black Start resources to obtain emission permit waivers to accommodate operations during a restoration situation (operating below normal economic min values), if required. | Same as PJM
3 | Non-Fuel Consumables (eg. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement. | Capable of supporting the duration of the run hour requirement. | Same as PJM | Same as PJM | Same as PJM | Capable of supporting the duration of the run hour requirement. | Same as PJM
4 | Bilateral Compensated Black Start resource Requirements |  | NERC Requirements | Must meet all fuel assurance requirements to be considered a fuel assured Black Start resource. Must enter PJM Black Start service through RFP process. | Definition required. Must meet all fuel assurance requirements to be considered a fuel assured Black Start resource. Must enter PJM Black Start service through RFP process. | Must enter PJM's market RFP and be shown to be more economic than alternatives. | Same as PJM | Same as PJM | Must meet all fuel assurance requirements to be considered a fuel assured Black Start resource | Same as PJM
5 | Starting System Requirements |  | N/A | Capability to provide a minimum of 3 starts over the course of 16 hours. | Capability to provide a minimum of 3 starts over the course of 16 hours Should capability for more starts be required? |  | Same as PJM | Same as PJM | Capability to provide 3 starts with a minimum 16 hours idle time | Same as PJM
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Not allowed to be a fuel assured Black Start without on-site fuel capability, interconnection to multiple interstate pipelines with separate laterals into the plant, or is located in close proximity to a natural gas gathering facility (ahead of gas transmission system) and the generator can provide documentation to PJM that the facility will be able to provide uninterruptible gas supply during a loss of off-site power supply (i.e. black out). | Options in addition to on-site fuel should be considered including multiple pipeline interconnections, nature of gas supply arrangements, special pipeline rules for system restoration, or location of gas supply. | Same as PJM | Fuel assurance can be met though a variety of means including on-site storage, multiple pipelines, energy storage, and resource diversity. | Fuel assurance can be met though a variety of means including on-site storage, multiple pipelines, energy storage, and resource diversity. | - Dual fueled units capable of starting solely on on-site fuel OR - Gas only units connected to multiple interstate gas pipelines OR - Gas only unit connected to a single gas source fed directly from a gas supply basin / gathering system ahead of interstate pipelines (PJM will validate all contractual arrangements for gas supply/delivery) | Same as PJM
2 | Oil | High | 16 hours of run hour requirements | Sufficient oil storage on-site at all times for each Black Start resource at a site to meet minimum run time requirements (if resources share the same fuel source) | Sufficient oil storage on-site at all times for each Black Start resource at a site to meet minimum run time requirements (if resources share the same fuel source) | Same as PJM | Same as PJM | Same as PJM | Sufficient fuel oil stored on-site at all times for each Black Start resource in a site to meet minimum run time requirements (if resources shares the same fuel source) | Same as PJM | Low - High
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Run of River and Pumped Storage Hydro will be able to choose between a 10 hour or 16 hour minimum run requirement (or as defined by TO restoration plan) at full load. Units on the Base Formula Rate may choose between a 10 hour or 16 hour minimum requirement with the tiered options identified in the PJM Hydro Proposal document. Run of River Hydro with or without Storage shall use the daily volumetric inflow values for the past 20+ years from the appropriate USGS river flow gauges or other instrumentation agreed to by the Hydro Generation Owner and PJM with input from IMM to determine the maximum number of black start MW that can be supported for chosen minimum run hour requirement (10 or 16 hours). Run of River Hydro with storage can use the normal, daily starting elevation levels for storage values within licensing limits in the Black Start MW calculation with PJM concurrence. The Black Start MW calculation shall be based on river flows of 90% confidence level based on monthly average of daily flows to correspond to the current average PJM CT Equivalent Availability Factor. | Analysis with 90% of confidence of most restrictive seasonal flow to support the assigned Black Start MW. Confidence level needs to be defined and comparable to other resources. Drought conditions should be analyzed. No facility costs should be assigned to black start service. | 24 hours of run hours requirements | Same as PJM | Same as PJM | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM PJM calculates both fuel assured and non-fuel assured hydro resource’s confidence level using unit specific historical data submitted to PJM for the ELCC analysis performed in December 2021. This historical data includes hourly streamflow data, minimum & maximum flows, and exigent & ordinary storage converted into MWh. For non-fuel assured resources, PJM calculates a yearly confidence level (non-fuel assured resources) based on a simple average of the number of days the unit can provide its black start ICAP for 16 hours in a day. The overall confidence level for the historical years is calculated using a ELCC weather weighted average. For fuel assured resources, PJM iterates the Black Start MWs in the no-fuel assured calculation to obtain an ELCC weather weighed confidence level of 90%. | Same as PJM except for a Monthly MW 90% confidence level assessment, instead of an annual assessment | Medium
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | Run of River and Pumped Storage Hydro will be able to choose between a 10 hour or 16 hour minimum run requirement (or as defined by TO restoration plan) at full load. Units on the Base Formula Rate may choose between a 10 hour or 16 hour minimum requirement with the tiered options identified in the hydro proposal document. | The pond level must satisfy run hour requirements to meet the Black Start commitment. No facility costs should be assigned to black start service. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) | Same as PJM | Same as PJM | The pond level must be maintained to satisfy run hour requirements to meet the Black Start commitment. | Same as PJM | Medium - High
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Stored Energy Resource analysis of MW capability based on confidence level similar to CT EAF. | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) Stored energy must always be kept on-site for each Black Start resource to meet minimum run time requirements. | Stored Energy Resource analysis of MW capability based on confidence level similar to CT EAF. | Stored Energy Resource analysis of MW capability based on confidence level similar to CT EAF. | The storage level must be maintained to satisfy run hour requirements to meet the Black Start commitment. | Same as PJM | High
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Hybrid Resource analysis of MW capability based on confidence level similar to CT EAF. | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) A combination of on-site fuel inventory, water level, stored energy, etc. must always be kept on-site for each Black Start resource to meet minimum run time requirements | Hybrid Resource analysis of MW capability based on confidence level similar to CT EAF. | Hybrid Resource analysis of MW capability based on confidence level similar to CT EAF. | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM and meet all requirements in Design Component Section B and PJM OATT Schedule 6A | Same as PJM except for a Monthly MW 90% confidence level assessment, instead of an annual assessment
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Intermittent Resource analysis of MW capability based on confidence level similar to CT EAF. | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage. | Same as PJM | Same as PJM | Ability to provide black start MW for the minimum run time duration with 90% confidence as calculated by PJM and meet all requirements in Design Component Section B and PJM OATT Schedule 6A PJM calculates both fuel assured and non-fuel assured intermittent resource’s confidence level using unit specific historical data submitted to PJM for the ELCC analysis performed in December 2021. For non-fuel assured resources, PJM calculates a yearly confidence level (non-fuel assured resources) based on a simple average of the number of days the unit can provide its black start ICAP for 16 hours in a day. The overall confidence level for the historical years is calculated using a ELCC weather weighted average. For fuel assured resources, PJM iterates the Black Start MWs in the no-fuel assured calculation to obtain an ELCC weather weighed confidence level of 90%. | Same as PJM except for a Monthly MW 90% confidence level assessment, instead of an annual assessment
8 | DER/DR with on-site generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | DER/DR Resource analysis of MW capability based on confidence level similar to CT EAF. | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage. | DER/DR Resource analysis of MW capability based on confidence level similar to CT EAF. | DER/DR Resource analysis of MW capability based on confidence level similar to CT EAF. | Meet all requirements in Design Component Section B and PJM OATT Schedule 6A | Same as PJM
D | Fuel Assurance Testing & Verification Requirements (for Fuel Assured Resources Only)
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel in the same year | Same as PJM. Paid for testing. | Same as PJM | Same as PJM | Separate testing for each fuel in the same year | Same as PJM
2 | Concurrent fuel testing | High | None | Status Quo | All Black Start resources connected to the same fuel source test concurrently | Same as PJM. Applies to more than Oil/Gas units. Paid for testing. | Same as PJM | Same as PJM | None (Status Quo) | Same as PJM
3 | Online fuel transition testing | Medium | None | Provide data annually on fuel switching restrictions/limitations that unit may have. Documentation would be in the form of a copy of the procedure used to switch fuels. It would be uploaded with annual BS test procedure. | One test per year to demonstrate the ability to switch between fuels. | Same as PJM. | Same as PJM | Same as PJM | None (Status Quo) | Same as PJM
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Based on resource unit and fuel type, on-site fuel inventory, water level, stored energy, etc. limitations must be communicated as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting and (if possible) telemetry, for situational awareness | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM. | Same as PJM | Same as PJM | Fuel Assured units must provide fuel/energy verification to PJM every six months or upon PJM request. Fuel/energy level telemetry to PJM is an acceptable form of verification. For natural gas resources, PJM will validate all contractual arrangements for gas supply/delivery. | Same as PJM
5 | Starting Systems verification |  | n/a | Starting system limitations must be communicated as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if starting systems not able to meet the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM | Same as PJM | Same as PJM | Fuel Assured units must communicate starting system limitations as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if starting systems not able to meet the run time requirement | Same as PJM
6 | Non-Fuel Consumables (eg. water, ammonia) inventory verification |  | n/a | Non-fuel consumables inventory limitations must be communicated as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if consumables fall below the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM | Same as PJM | Same as PJM | Fuel Assured units must communicate non-fuel consumables inventory limitations as soon as possible but within one hour of recognition to PJM via Markets Gateway Resource Limitation Reporting if consumables fall below the run time requirement | Same as PJM
7 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability based on the most limiting season, if applicable. | Black Start capability based on 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) | Same as PJM | Same as PJM | Either the unit's ICAP or the PJM determined MW with 90% confidence is used for unit compensation | Same as PJM except for a Monthly MW 90% confidence level assessment, instead of an annual assessment
8 | Black start MW capability verification | High | The annual capacity test | Status Quo | All Black Start resources connected to the same fuel source test concurrently | Same as PJM. Paid for testing. | Same as PJM | Same as PJM | Annual capacity test (Status Quo) | Same as PJM
9 | Emission permit limitation verification |  | None | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable. | Black start resource owners will certify using written waivers or other applicable documentation that waivers of emission permit limitations are available during restoration operations, as applicable. | Same as PJM. | Same as PJM | Same as PJM | TBD | Same as PJM
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours AND Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance. PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for Black Start by netting energy revenues (Max (0, DA Credits + RT Credits - Cost)) that are a direct result of the capital expenditures during the capital recovery period. Energy revenues will be netted from monthly Black Start Credits on a monthly basis. If the energy revenues exceed the monthly black start revenues, the residual will be carried to subsequent months until all energy revenues have been netted. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A for the required fuel levels defined by required run time hours. Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance, capital costs submitted and approved in accordance with the schedule 6A process. Unit owners submitting costs for fuel storage must separately account for all cost associated with the development and building of the storage and submit third party independent verification of the storage tank MTSL. | Same as PJM | Same as PJM | Same as PJM | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours | Same as PJM
1 | Fuel Assurance Compensation Capital Recovery Period. |  | N/A | Fuel Assurance Capital cost will be recovered using a new Schedule 6A Fuel Assurance 20 year CRF recovery period. For units with ages greater than 20 years, PJM at its option, may choose to use the new Schedule 6A 10 year CRF recovery period. Regardless of recovery period, the unit will also commit to provide Black Start Service for for the remainder of its life. After completion of the capital recovery period, compensation would be on the base formula rate. **TABLE** 20 Year CRF - 0.096 10 Year CRF - 0.144 *CRF rates are calculated based on the current tax law that is valid for fuel assurance upgrades completed through 2022 | Fuel Assurance Capital cost will be recovered using a new Schedule 6A Fuel Assurance 20 year CRF recovery period unless the unit is at least 20 years old in which case using a 10 year CRF recovery period. Regardless of recovery period, the unit will also commit to provide Black Start Service for for the remainder of its life. After completion of the capital recovery period, compensation would be on the base formula rate. The CRF rates will be reviewed annually and updated as needed. The same CRF values will be used for all black start capacity cost recovery. | Existing Schedule 6A recovery period based on age of unit | Same as PJM. | Same as PJM. | The greater of the schedule 6A recovery period based on the age of the unit or 10 years. | Same as PJM
2 | Portion of fuel assured capital recovery that is solely necessary for Black Start |  | N/A |  | Only the allocated share, based on the 16 hour black start requirement, of any new fuel related investment should be included in black start rates when such investment is also used for capacity market or energy market purposes. |  |  |  | In order to determine how much of the capital recovery is solely necessary for Black Start, any energy revenues obtained as a result of a fuel assurance conversion minus the unit’s cost to provide those MWs, by month, would be netted from the black start revenues for that month. | Same as PJM
| Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG Black Start resources are compensated for carrying cost of the full MTSL volume. For Black Start resources that share tanks only one unit gets compensated. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank's usable capacity (tank size minus tanks MTSL) capacity times the MTSL. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank's usable capacity (tank size minus tanks MTSL) capacity times the MTS as outlined in schedule 6A. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 24 hours divided by the average daily tank level from prior delivery year times the MTSL. | Same as PJM | Same as PJM
3 | Onsite fuel, water level, stored energy, etc., starting systems and non-fuel consumables compensation | Medium | None | Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy, or non-fuel consumables falls below the run hour requirement as the result of a regulatory requirement, an approved outage, or restoration event, monthly Black Start revenues will not be withheld. If fuel inventories fall below 16 hr including for a PAI event, monthly Black Start revenues will be foregone. | If the on-site fuel inventory, water level, stored energy, etc., starting systems, or non-fuel consumables falls below the run hour requirements for any length of time during any period, PJM dispatch must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy falls below the run hour requirement as the result of an approved planned outage (full derate), monthly Black Start revenues will not be withheld. | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient, except if do to an implemented PAH or actual system restoration. | Same as IMM | Same as IMM | If the on-site fuel inventory, water level, stored energy, etc. of a Fuel Assured black start resource falls below the run hour requirements for any length of time during any period, PJM dispatch must be notified within 24 hours. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. If the fuel inventory, water level, stored energy falls below the run hour requirement as the result of a regulatory requirement for approved planned outage (full derate), monthly Black Start revenues will not be withheld. | Same as PJM
4 | Fuel Assurance Testing Compensation |  | None | Units will be compensated for fuel assurance testing on both fuels. | Units will be compensated for fuel assurance testing on both fuels. | Same as PJM | Same as PJM | Same as PJM | Units will be compensated for fuel assurance testing on both fuels. | Same as PJM
5 | Compensation for non-CRF Black Start resources and non Black Start resources that do not require capital projects to provide fuel assured black start. |  | Base formula rate | For Fuel Assurance Black start resources, base formula rate compensation incentive factor changed to Z=0.2 (from Z=0.1) | For Fuel assurance Black Start resources, base formula rate compensation incentive factor should remain the same Z=0.10 | Same as PJM |  |  | Staus Quo, Z factor = 10% | Same as PJM
6 | Run of River Hydro Compensation |  | Base formula rate | Tier 1: 90% Confidence level for 16 hour minimum run requirement. Allocation X factor = 0.02 and Incentive Z factor = 20%. Monthly validation: None. Tier 2: 90% Confidence level for 10 hour minimum run requirement (or as defined by TO restoration plan). Allocation X factor = 0.01 and Incentive Z factor = 10%. Monthly validation: If a 10 hour or greater minimum run requirement is used, a monthly verification will take place to determine if unit(s) could meet assigned MW requirement for 16 hour run time based on average monthly flow. If capable of meeting, Incentive Z factor is increased to 20% for the Month's Base Formula Rate. Units will need to provide one years notice to switch tiers. New units on the Capital Recovery Rate will specify the Tier of service they will provide when they submit their initial proposal. | 90 % confidence level for 10 to 16 hours minimum run requirement. Allocation X factor = 0.01 and incentive factor = 10% |  | Same as PJM | Same as PJM | Non-fuel assured run of river black start sites is base formula rate (status quo). Fuel assured run of river black start sites Allocation X factor = 0.02 and Incentive Z factor = 10%. | Same as PJM except fuel assured black start sites are compensated based on a Monthly MW 90% confidence level assessment, instead of an annual assessment
7 | Pumped Storage Hydro Compensation |  | Base formula rate | Same as Run of River | 90 % confidence level for 16 hours minimum run requirement. Allocation X factor = 0.01 and incentive factor = 10% |  | Same as PJM | Same as PJM | Non-fuel assured pumped storage black start sites is base formula rate (status quo). Fuel assured pumped storage black start sites Allocation X factor = 0.02 and Incentive Z factor = 10%. | Same as PJM
8 | Energy Storage, Hybrid, Intermittent Resources Compensation |  |  |  | 90 % confidence level for 16 hours minimum run requirement. Allocation X factor = 0.01 and incentive factor = 10% |  |  |  | Non-fuel assured black start sites is base formula rate (status quo). Fuel assured black start sites Allocation X factor = 0.02 and Incentive Z factor = 10%. | Same as PJM except fuel assured black start sites are compensated based on a Monthly MW 90% confidence level assessment, instead of an annual assessment
9 | Cost Allocation |  | Black start resource annual revenue requirements by zone are allocated to point to point reservations and network zonal load on a peak load share basis (Schedule 6A, paragraph 25) | Status Quo | system wide allocation or status quo |  | Status Quo | Status Quo | Status Quo | Same as PJM
F | Implementation |  | N/A
1 | Implementation Date | [7 empty] | New business rules would take effect 2023 RTO-Wide RFP and onwards | Same as PJM
2 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service Existing fuel assured Black Start resources do not have to submit a proposal into the RFP process. Existing non-fuel assured Black Start resources that do not offer into the RFP may be terminated. Non-fuel assured Black Start resources already on a capital recovery rate would not be terminated until after the capital cost recovery term has been completed, however these black start resources will not be used to meet Manual 36 Critical Load requirements. | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service. Black Start resources should not be terminated until after the capital cost recovery term has been completed and after the obligation to provide service for life of asset. Non fuel assured resources can continue to provide black start service. | Same as PJM. | Same as PJM | Same as PJM | Existing non-fuel assured black start sites can participate in future RFPs with fuel assured proposals PJM will conduct outreach to black start units to validate fuel assurance status ahead of each RTO-wide RFP. Participating as a fuel assured black start unit is voluntary and non-fuel assured resources can continue to provide black start service. | Same as PJM
3 | New Black Start resources | High | None | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | Same as PJM. | Same as PJM | Same as PJM | New black start sites can participate in future RFPs with both fuel assured and non-fuel assured proposals | Same as PJM
4 | Procuring additional Black Start resources because of immediate deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Existing incremental RFP process would be used | Same as PJM. | Same as PJM | Same as PJM | Existing incremental RFP process would be used | Same as PJM
5 | Reliability Backstop |  | PJM Manual M14D Section 10.3 |  | TOs should not be permitted to own generation. Status Quo |  |  |  | Existing Reliability Backstop Process in PJM Manual M14D Section 10.3 to be implemented in the event of insufficient response to RTO wide RFP or future incremental RFP (2 failed RFP processes), to meet minimum of one black start site per zone meeting fuel assurance criteria and reliability (PLUS) criteria beyond minimum criteria for high impact black start sites. For Reliability Backstop RFP, TO required to submit RFP proposal. | Same as PJM

## 3a. Package Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3