## Setup
Enter Stakeholder Committee Name in cell A2:
DER and Inverter-based Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Hybrid Resources Phase II

## 1. Interest Identification
DER and Inverter-based Resources
Hybrid Resources Phase II
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure that solar-battery hybrid resources mixed technology facilities in the PJM interconnection queue have a clear understanding of the rules and requirements that apply to this resource type for the purposes of participation in PJM energy and ancillary services markets.
2 | Consideration of unique operational aspects of solar-battery hybrid resources.
3 | Operational visibility of each resource type, in real time, within a hybrid resource.
4 | Ensure the ability of dc-coupled hybrids to make use of co-located resources for charging the storage resource without incurring undue costs, such as for transmission or schedule deviations
5 | Ensure that well defined parameters and clear market rules are provided for all different potential configurations and that the parameters are coordinated between operations, markets and planning.
6 | Ensure that there are clear PJM Planning rules regarding changing project configurations once the study process has started.
7 | Ensure that PJM planning and operations are in agreement with how potential hybrid configurations will impact a resource's ability to charge or not charge from the grid.
8 | Ensure that metering provided to PJM Settlements is also sufficient for purposes of creating Renewable Energy Credits.
9
10
11
12
13
14
15
16
17
18

## 2. Options Matrix- Design Comp.
DER and Inverter-based Resources
Hybrid Resources Phase II
OPTIONS MATRIX
Updated: June 2022
Solution Options2
# | Design Components1 | Priority | Status Quo (incl. Hybrids Phase 1) | A | B | C | D | E | F
* | Implementation
Markets Items
0a | Co-Located Resources: calculation of Effective Nameplate Capacity (ENC) |  | Maximum Facility Output is allocated to components for use in calculating ENC (M21A Section 4.1). | Clarify and add detail to the status quo: The Maximum Facility Output at a Mixed Technology Facility shall be fully allocated to its component Co-Located Resources. The ENC of a Co-Located Resource that is Variable Resource or a Combination Resource is equal to its allocation of Maximum Facility Output. The ENC of a Co-Located Resource that is a Limited Duration Resource is equal to its allocation of Maximum Facility Output multiplied by the ratio of the duration of the resource to the duration of its class.
1 | Definitions, including classification of hybrids relative to existing resource types (e.g., Intermittent Resource, Energy Storage Resource, etc). |  | See slide 3 for definitions: https://www.pjm.com/-/media/committees-groups/subcommittees/dirs/2022/20220429/20220429-item-05-hybrid-resources-phase-ii.ashx [Starting June 1, 2023] - Any Hybrid Resource may participate in PJM markets | Hybrid Resource definition includes any Mixed Tech Facility participating in markets as a single unit (ie, including any mix of any numer of generation and/or storage technology types). (Note: this means additional types of Hybrid Resources inherit the right to participate in PJM markets, e.g., hydro+battery or hydro+solar hybrid). Provisions that apply to a type of inverter-based standalone Variable Resource (e.g., wind, solar, intermittent hydro) do not apply to a Hybrid Resource with a component of that technology type, unless otherwise specified.
2 | Modeling Energy/Ancillary Services for Hybrids |  | Solar+battery hybrids use similar model as Energy Storage Resource Model Participants | Inverter-based gen+storage Hybrid Resources (e.g., any mix of wind and solar plus battery) use similar energy model as solar-storage hybrids. For storage Hybrids, "Variable only" mode indicates when battery is idle. Inverter-based gen-only Hybrid Resources (e.g., wind+solar) use similar energy model as wind.
3 | Market Operations of negative MW for Open Loop Hybrids |  | Solar+battery hybrids use similar model as Energy Storage Resource Model Participants | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
4 | Regulation for Hybrids |  | Solar+battery hybrids use similar model as Energy Storage Resource Model Participants, except no Reg-only | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
5 | Reserves for Hybrids |  | Solar+battery hybrids use similar model as Energy Storage Resource Model Participants, except no Reserves-only | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
6 | Capacity Market must offer for Hybrids |  | Intermittent Resources, Capacity Storage Resources, Demand Resources, Energy Efficiency Resources, and Hybrid Resources consisting of only Intermittent and Storage components, are not required to submit a Capacity Performance sell offer segment. | No change to hybrids phase 1 (a hybrid with components that are exempt from the RPM must offer is itself exempt).
7 | Energy Market must offer for Hybrid Capacity Resources |  | Intermittent Resources, Energy Storage Resources, and Hybrid Resources consisting of only Intermittent and Storage components, may offer quantities that vary from their cleared UCAP quantity | No change to hybrids phase 1 (a hybrid with components with obligatory energy offers that vary hourly, themselves have obligatory energy offers that vary hourly).
8 | Billing and settlements for charging energy of open-loop hybrids |  | Charging energy for Energy Storage Resource Model Participant and Open-Loop Hybrid Reesources takes transmission service under certain circumstances (consistent with Order 841), and therefore pays additional non-LMP charges sometimes. See Manual 27 Section 8 and Manual 28 Section 22. | Same as phase 1 hybrid rules.
9 | Number of resources for MOPR purposes for a Hybrid |  | Hybrid Resources are considered one resource and would be modeled as one resource for MOPR. See OATT Attachment DD 5.14.
10 | Resource Classification Process for Mixed Technology Facilities |  | ELCC limits changes in class to once per five years. Hybrids phase 1: eligible Energy-only Hybrids under phase 1 proposal can change classification once per year.
11a | Uplift for Hybrids |  | Hybrid Resources are eligible for Reactive Services uplift and discussion of mutually acceptable lost opportunity cost compensation; Solar is not eligible for those things. | Categorical eligibility is same as hybrids phase 1. Quantity of solar+wind hybrid LOC cannot exceed sum of wind+solar forecast. Quantity of storage+variable hybrid cannot exceed variable_forecast+storage_nameplate, except when state of charge is zero or resource is in "variable only" mode, the LOC quantity cannot exceed variable_forecast.
12 | Market Settlement to Multiple Members for Hybrids |  | In certain circumstances, a single resource may be eligible to split market settlements among multiple Members
Operations Items
13 | Telemetry & Metering for Hybrids *Accuracy is at a system level |  | Settlement meter required at POI. To the extent state or jurisdictional rules allow Certificates to be created for generation that is not delivered to the transmission grid, PJM EIS has procedures in place to do so, as described in the GATS Operating Rules. See Tab 2b, Option Details, for further explanation. | Same as hybrids phase 1: settlement meter at POI, and SCADA measurement devices for aggregate MW of each technology type component. | [5 empty] | Low - High
14 | Telemetry & Metering for Co-Located Facilities *Accuracy is at a system level |  | SCADA metering required for POI, and also for aggregate MW output of components. | Same as hybrids phase 1.
15 | Data Requirements for Forecasting for Hybrids |  | Solar (M-14D, Section 12.2): Static requirements (12.2.1) Real-time output (12.2.2) - 3MW or greater. "If a solar park is collocated with an energy storage facility such as a battery, then separate metering is required for each component in order to preserve solar forecast accuracy." Real-time meteorological data (12.2.3) | Hybrids with a wind or solar component have same data requirements as standalone wind or solar, respectively. | [5 empty] | Medium - High
16 | Operating requirements for Hybrids |  | An Hybrid Resources’s Economic Minimum shall not exceed the level of its CIR... An Hybrid Resource’s Emergency Minimum should be set to 0... Hybrid Resource curtailment should be achieved within 5 minutes or consistent with the resources ramp rate bid. PJM should be notified if curtailment is expected to exceed 5 minutes.
17 | Outage Reporting for Hybrids |  | Separate reporting in eDART for each component of a hybrid resource. GADS reporting for the storage component of a hybrid resource. | Same as hybrids phase 1 | [5 empty] | High
18 | Reactive Capability: testing |  | Solar: variable MW output Inverter-based Storage: MAX MW (full lead and lag) ZERO MW output (max lead and lag) MIN MW output (i.e., max charging) (max lead and lag)
19 | Reactive Capability: D-curves |  | All resources: The “Unit Minimum and Maximum Net MVAR Limits” must indicate the realistic, usable capability that is sustainable during continuous long-term unit operation. ESR: For inverter-based Energy Storage Resources, the reactive capability should be based on Inverter MVA Capability Curve.
Cost Development Subcommittee items--new Issue Charge required for changes to status quo
20 | Cost Offers for Hybrids |  | Cost Offers of $0 are acceptable, other cost offer methods must follow rules in Manual 15 | Same as phase 1 hybrid rules.
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
DER and Inverter-based Resources
Hybrid Resources Phase II
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
DER and Inverter-based Resources
Hybrid Resources Phase II
SOLUTION OPTION DETAILS
Updated: May 14, 2021
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description

## 3. Package Matrix
DER and Inverter-based Resources Subcommittee
Solar-Battery Hybrids Resources
PACKAGE/ PROPOSAL MATRIX
2022-06-15
# | Design Components | Priority | A | B | C | D
* | Implementation
Markets Items
0a | Co-Located Resources: calculation of Effective Nameplate Capacity (ENC) |  | Clarify and add detail to the status quo: The Maximum Facility Output at a Mixed Technology Facility shall be fully allocated to its component Co-Located Resources. The ENC of a Co-Located Resource that is Variable Resource or a Combination Resource is equal to its allocation of Maximum Facility Output. The ENC of a Co-Located Resource that is a Limited Duration Resource is equal to its allocation of Maximum Facility Output multiplied by the ratio of the duration of the resource to the duration of its class.
1 | Definitions, including classification of hybrids relative to existing resource types (e.g., Intermittent Resource, Energy Storage Resource, etc). |  | Hybrid Resource definition includes any Mixed Tech Facility participating in markets as a single unit (ie, including any mix of any numer of generation and/or storage technology types). (Note: this means additional types of Hybrid Resources inherit the right to participate in PJM markets, e.g., hydro+battery or hydro+solar hybrid). Provisions that apply to a type of inverter-based standalone Variable Resource (e.g., wind, solar, intermittent hydro) do not apply to a Hybrid Resource with a component of that technology type, unless otherwise specified.
2 | Modeling Energy/Ancillary Services for Hybrids |  | Inverter-based gen+storage Hybrid Resources (e.g., any mix of wind and solar plus battery) use similar energy model as solar-storage hybrids. For storage Hybrids, "Variable only" mode indicates when battery is idle. Inverter-based gen-only Hybrid Resources (e.g., wind+solar) use similar energy model as wind.
3 | Market Operations of negative MW for Open Loop Hybrids |  | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
4 | Regulation for Hybrids |  | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
5 | Reserves for Hybrids |  | Inverter-based storage Hybrid Resources (e.g., any mix of wind and solar including also a battery) use similar energy model as solar-battery hybrids.
6 | Capacity Market must offer for Hybrids |  | No change to hybrids phase 1 (a hybrid with components that are exempt from the RPM must offer is itself exempt).
7 | Energy Market must offer for Hybrid Capacity Resources |  | No change to hybrids phase 1 (a hybrid with components with obligatory energy offers that vary hourly, themselves have obligatory energy offers that vary hourly).
8 | Billing and settlements for charging energy of open-loop hybrids |  | Same as phase 1 hybrid rules.
9 | Number of resources for MOPR purposes for a Hybrid |  | Status quo
10 | Resource Classification Process for Mixed Technology Facilities |  | Status quo
11a | Uplift for Hybrids and Storage |  | Categorical eligibility is same as hybrids phase 1. LOC cannot exceed Maximum Facility Output. [Following edits for clarity]. Quantity of solar+wind hybrid LOC cannot exceed sum of wind+solar forecast. Quantity of storage+variable hybrid cannot exceed variable_forecast+storage_nameplate, except when state of charge is zero or resource is in "variable only" mode, the LOC quantity cannot exceed variable_forecast. To the extent that a wind/solar hybrid or battery parameter does not properly reflect the unit’s capability, PJM reserves the right to limit LOC to the more accurate parameter value. a. E.g., an empty battery has LOC limited to 0 MW b. E.g., a solar/wind hybrid with empty battery (or no battery, or in variable-only mode) has LOC limited to the solar/wind backcast c. E.g., a solar/wind hybrid with non-empty battery has LOC limited to the solar/wind backcast plus battery_nameplate_MW
12 | Market Settlement to Multiple Members for Hybrids |  | Status quo
Operations Items
13 | Telemetry & Metering for Hybrids *Accuracy is at a system level |  | Same as hybrids phase 1: settlement meter at POI, and SCADA measurement devices for aggregate MW of each technology type component.
14 | Telemetry & Metering for Co-Located Facilities *Accuracy is at a system level |  | Same as hybrids phase 1. Separate MW and MVAR SCADA submeters required for each component. No settlement submeters required.
15 | Data Requirements for Forecasting for Hybrids |  | Status quo [Package language is same as status quo for hybrids phase 1] Hybrids with a wind or solar component have same data requirements as standalone wind or solar, respectively.
16 | Operating requirements for Hybrids and Storage |  | Same as hybrids phase 1, plus: [Reworded for clarity]: 1. Variable+battery hybrid ECOMAX should not exceed battery_nameplate_MW plus anticipated_variable_availability when the battery is not empty (where variable can be wind, solar, hydro, or other Variable Resource). 2. Variable+battery hybrid ECOMAX should not exceed anticipated variable availability when the State Of Charge of the battery component is at or below the Minimum State Of Charge (i.e., it is empty), or if there is no battery (e.g., wind+solar hybrid). 3. ECOMAX of an Energy Storage Resource Model Participant should not exceed 0 when the State Of Charge is at or below the Minimum State Of Charge (i.e., it is empty). 1. Wind/solar hybrid ECOMAX should not exceed battery_nameplate_MW plus anticipated_wind/solar_availability. 2. Wind/solar hybrid ECOMAX should not exceed anticipated wind/solar availability when the State Of Charge of the battery component is at or below the Minimum State Of Charge (i.e., it is empty), or if there is no battery (i.e., wind+solar hybrid). 3. ECOMAX of an Energy Storage Resource Model Participant should not exceed 0 when the State Of Charge is at or below the Minimum State Of Charge (i.e., it is empty).
17 | Outage Reporting for Hybrids |  | Same as hybrids phase 1
18 | Reactive Capability: testing |  | Same as hybrids phase 1
19 | Reactive Capability: D-curves |  | Same as hybrids phase 1
High
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
DER and Inverter-based Resources
Hybrid Resources Phase II
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
DER and Inverter-based Resources
Hybrid Resources Phase II
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
DER and Inverter-based Resources
Hybrid Resources Phase II
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1 |  | April 2022 initial draft
2
3