## Open Questions
Question Created Date | Question Created By | Title | Body
2020-01-27 | AMP | AEP-2018-AP010 | In regards to AEP's proposed solution to address need number AEP-2018-010 please provide the followings details and responses to the questions below: 1. Life expectancy of the proposed solution as compared to that of the Alternative considered 2. Parameters and requirements used to size the battery storage project 3. Overall size and MWh capability of the battery 4. Additional details regarding the voltage level at which the battery will connect to the transmission system. Will it connect at distribution level voltages or will it connect directly to the 69kV network. Does AEP's cost include cost to connect the battery. 5. What referenced criteria or assumption were used to quantify the need for the battery installation. 6. Under what situations will the proposed battery operate? For example when the radial line is out of service. 7. Will the battery participate as a PJM market participant including but not limited frequency regulation, energy or capacity? 8. Will the battery be owned by AEP's Kentucky Power Company or will it be owned by AEP's Kentucky Transco company? 9. Will the battery enter into the PJM generation connection queue? 10. What organization will control the dispatch of the battery resource, AEP Transmission or PJM? 11. For what period of time has the line between AEP's system and EKPC's system operated normally open?
2020-01-31 | AMP | Batteries and Other Energy Storage devices | Does the PJM OA definition of "Transmission Facilities" include Batteries or Storage devices? If so, what parameters or test must a battery or storage device meet to be determined as transmission?
2020-02-03 | AMP | 2019 RTEP statistics | Will PJM be providing 2019 RTEP statistics similar to those provided for 2017 and 2018 RTEP planning years?
2020-02-06 | LS Power | AEP-2018-AP010 | LS Power has questions about AEP-2018-AP010, as presented at a recent January 2020 Subregional TEAC meeting. The project proposes a 2 MW BEES solution at Middle Creek Substation, as a supplemental Project. A supplemental project must meet the definition of a Transmission Facility under the PJM Operating Agreement, in order for the Transmission Facility to be included in the RTEP (and meet the RTEP definition of Transmission). This battery has not had a FERC ruling classifying it as Transmission; therefore, it does not meet the definition of Transmission Facilities in the Operating Agreement. It is not eligible to included in the Supplemental Project category. In addition, we have overarching concerns about setting the precedent of batteries in Supplemental Project category
2020-02-07 | Sonny Nguyen | Correct line rating | Which case has the correct line rating for Laurel to Short 69 kV line? Is it 57 MVA or 93 MVA? I'm looking at the cases: MMWG_2024SUM_2019Series_Final.sav and 2023_AF1_Queue_Study_Summer_NonDiv_MTX_Op1.sav.
2020-02-18 | DTE Energy | AEP-2018-AP010 | Please provide a summary of the AEP-2018-AP010 supplemental project that contemplates the installation of a battery at the upcoming MRC meeting on February 20,2020. This would seem to have overarching public policy implications that should be discussed.
2020-05-01 | AMP | Transmission Owner's Finalized 2019 Local Plans | Can PJM provide copies of all transmission owner's finalized local plans resulting from the M3 process? It seems that the 2019 plans are no longer posted on PJM's website but the 2020 plans are.
2020-05-19 | AMP | 2019 Project Statistics | Can PJM post or make available the data sets used to develop the 2019 project statistics slides reviewed at the 5-12-2019 TEAC meeting?
2020-05-21 | Energy Authority, Inc. | B3098 Scope and Cost Modification in May 2020 SRRTEP Southern Meeting | The driver of the project is transmission line. The scope modification includes station work at Balcony which was not included in the baseline problem statement. Should station work portion be a supplemental project? In addition, what is the applicability of End-of-Life criteria at different voltage level?
2020-06-03 | AMP | Doub's - Goose Creek 500kV End-of-Life Reliability Violation | In PJM's TEAC presentation from 6/2/2020​, PJM noted in bullet item #3 that a stability (non-convergence) issue was identified using PJM's Winter 2025 RTEP models after the Doubs - Goose Creek 500kV line was remove from service and a single contingency outage of the Bismark - Doubs 500kV line. In this analysis, was the requested generation deactivation of Dickerson Units 1,2,3 represented? Also, what units were identified as having stability issues leading to non-convergence?
2020-06-04 | AMP | 2020 Winter RTEP Model (Generation Dispatches by Fuel Type) | Based on our initial review of PJM's Preliminary 2020 Winter RTEP planning base case, It can been seen that the initial base case dispatches of the generators in the model do not match the percentage outlined in PJM Manual 14 B. For example: the vast majority of Solar facilities have their initial dispatches (PGen) vs. (PMax) set to 9% when Manual 14B calls for Solar facilities to be initially dispatched at 5%. A vast majority of Wind resources are being dispatched to 47% when the manual calls for 33%. Off-shore wind resources are dispatched to 61%. A number of Fossil Steam resources are dispatched between 41%-47% and 73%. Assuming these are coal recourses their target dispatches outlined in Manual 14B are between 51% for facilities < 500MWs, and 73% for facilities >= 500MW. Pump storage facilities are being dispatched to ranges of 55%, 70% & 100% when the manual calls for water resources to be dispatched at 38%. Last combined cycle resources believed to be natural gas are dispatched to level of 41%, 47%, 73% when the manual calls for 25%. AMP asked this specific question regarding the winter case dispatches matching the table outlined in Manual 14B at the last TEAC meeting. AMP was informed that the dispatches should match those outlined in the Manual 14B Exhibit 6: Table 1. If possible, could PJM clarify why the dispatch levels seem to significantly differ from those outlined in Manual 14B. If alternative dispatch levels are being used, will PJM be releasing updated dispatch target values for the winter case? AMP is bring this to PJM attention as there are currently 230kV facilities in the vicinity of <200kV overloads (currently excluded) from competition that are loading to 96% of their emergency capability for the same contingency event. AMP is concerned that these changes to the dispatch assumptions are significantly impact the contingency loadings on those facilities which is a cause for concern. Note: The facilities of concern are 232104 Mt PLSNT - 232106 MIDLTNTP 138kV (113.19%) for DPL_P7_1_DBL_INCB_FS(Tower), and Silver Run - Cedar Creek 230kV (currently 96%) for the same double circuit contingency event.