## BKR Rating Template
SUBSTATION EQUIPMENT RATING WORKSHEET
Circuit Breaker
1) Populate the nameplate information table as fully as possible
NAMEPLATE
STATION
EQUIPMENT |  |  | Circuit Breaker |  |  | Note: Correct system voltage must be entered for corresponding MVA values in the table below.
TYPE
YEAR MANUF.
MANUFACTURER |  |  | 1976
POSITION |  |  | ----
DESIGNATION |  |  | ----
RATED VOLTAGE (kV) |  |  | 230
RATED CURRENT (A) |  |  | 4000
2) Identify a material class and complete the input table
| Breakers manuf. Prior to 1964 | [5 empty] | Breakers manuf. 1964 and later
| 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6
qmax e4 | 85 | 90 | 110 | 135 | 85 | 95 | 105 | 120 | 120 | 165
qmax | 70 | 75 | 95 | 120 | 70 | 80 | 90 | 105 | 105 | 150
qr | 30 | 35 | 55 | 80 | 30 | 40 | 50 | 65 | 65 | 110
INPUT
qmax e4 | 120 |  |  | Rating |  | Summer 35o C |  | Winter 10o C
qmax | 105 |  |  |  |  | MVA | Amps | MVA | Amps
qr | 65 |  |  | Normal |  | 1660.4616 | 4168.1215 | 1967.4772 | 4938.7977
I Rated | 4000 |  |  | Emergency (4Hr) |  | 1849.5828 | 4642.857 | 2134.4275 | 5357.8796
Rated kV | 230
CALCULATED RATINGS
AMBIENT TEMP. |  | RATING ( P.U. ) |  |  |  | RATING ( MVA ) |  |  | RATINGS (AMPS) |  |  | `
qa | qa |  |  | Load |  |  |  | Load |  |  | Laod
Deg. C | Deg. F | NORMAL | 4 HOUR | Dump |  | NORMAL | 4 HOUR | Dump | NORMAL | 4 HOUR | Dump
-53.8889 | -65 | 1.6431 | 1.7275 | 2 |  | 2618.2078 | 2752.7694 | 3186.9735 | 6572.2737 | 6910.0528 | 8000
-51.1111 | -60 | 1.627 | 1.7121 | 2 |  | 2592.6788 | 2728.252 | 3186.9735 | 6508.1903 | 6848.5089 | 8000
-48.3333 | -55 | 1.6109 | 1.6966 | 2 |  | 2566.9471 | 2703.5571 | 3186.9735 | 6443.5981 | 6786.5192 | 8000
-45.5556 | -50 | 1.5946 | 1.681 | 2 |  | 2541.0073 | 2678.6804 | 3186.9735 | 6378.4837 | 6724.0733 | 8000
-42.7778 | -45 | 1.5782 | 1.6653 | 2 |  | 2514.854 | 2653.6175 | 3186.9735 | 6312.8331 | 6661.1599 | 8000
-40 | -40 | 1.5617 | 1.6494 | 2 |  | 2488.4812 | 2628.3638 | 3186.9735 | 6246.6318 | 6597.7675 | 8000
-37.2222 | -35 | 1.545 | 1.6335 | 2 |  | 2461.883 | 2602.9144 | 3186.9735 | 6179.8643 | 6533.884 | 8000
-34.4444 | -30 | 1.5281 | 1.6174 | 2 |  | 2435.0528 | 2577.2644 | 3186.9735 | 6112.5147 | 6469.4969 | 8000
-31.6667 | -25 | 1.5111 | 1.6011 | 2 |  | 2407.984 | 2551.4085 | 3186.9735 | 6044.5661 | 6404.593 | 8000
-28.8889 | -20 | 1.494 | 1.5848 | 2 |  | 2380.6695 | 2525.3413 | 3186.9735 | 5976.0008 | 6339.1586 | 8000
-26.1111 | -15 | 1.4767 | 1.5683 | 2 |  | 2353.102 | 2499.057 | 3186.9735 | 5906.8004 | 6273.1794 | 8000
-23.3333 | -10 | 1.4592 | 1.5517 | 2 |  | 2325.2737 | 2472.5497 | 3186.9735 | 5836.9452 | 6206.6402 | 8000
-20.5556 | -5 | 1.4416 | 1.5349 | 2 |  | 2297.1763 | 2445.8131 | 3186.9735 | 5766.4146 | 6139.5254 | 8000
-17.7778 | 0 | 1.4238 | 1.518 | 2 |  | 2268.8013 | 2418.8406 | 3186.9735 | 5695.1871 | 6071.8185 | 8000
-15 | 5 | 1.4058 | 1.5009 | 2 |  | 2240.1395 | 2391.6252 | 3186.9735 | 5623.2397 | 6003.5021 | 8000
-12.2222 | 10 | 1.3876 | 1.4836 | 2 |  | 2211.1812 | 2364.1599 | 3186.9735 | 5550.5482 | 5934.558 | 8000
-9.4444 | 15 | 1.3693 | 1.4662 | 2 |  | 2181.9164 | 2336.4368 | 3186.9735 | 5477.0869 | 5864.9671 | 8000
-6.6667 | 20 | 1.3507 | 1.4487 | 1.9772 |  | 2152.334 | 2308.4481 | 3150.6869 | 5402.8289 | 5794.7092 | 7908.9127
-3.8889 | 25 | 1.3319 | 1.4309 | 1.942 |  | 2122.4228 | 2280.1852 | 3094.5545 | 5327.7451 | 5723.7632 | 7768.0082
-1.1111 | 30 | 1.313 | 1.413 | 1.9063 |  | 2092.1705 | 2251.6392 | 3037.5955 | 5251.8052 | 5652.1066 | 7625.0285
1.6667 | 35 | 1.2937 | 1.3949 | 1.87 |  | 2061.5641 | 2222.8007 | 2979.7688 | 5174.9764 | 5579.7157 | 7479.871
4.4444 | 40 | 1.2743 | 1.3766 | 1.8331 |  | 2030.5897 | 2193.6598 | 2921.0301 | 5097.224 | 5506.5655 | 7332.424
7.2222 | 45 | 1.2546 | 1.3582 | 1.7956 |  | 1999.2327 | 2164.2058 | 2861.3308 | 5018.511 | 5432.6295 | 7182.5657
10 | 50 | 1.2347 | 1.3395 | 1.7575 |  | 1967.4772 | 2134.4275 | 2800.618 | 4938.7977 | 5357.8796 | 7030.1632
12.7778 | 55 | 1.2145 | 1.3206 | 1.7188 |  | 1935.3062 | 2104.3132 | 2738.8334 | 4858.0416 | 5282.2859 | 6875.0705
15.5556 | 60 | 1.194 | 1.3015 | 1.6793 |  | 1902.7016 | 2073.85 | 2675.9131 | 4776.1969 | 5205.8167 | 6717.1267
18.3333 | 65 | 1.1733 | 1.2821 | 1.639 |  | 1869.6438 | 2043.0245 | 2611.7862 | 4693.2145 | 5128.4381 | 6556.1542
21.1111 | 70 | 1.1523 | 1.2625 | 1.598 |  | 1836.1115 | 2011.8224 | 2546.3741 | 4609.0412 | 5050.114 | 6391.9555
23.8889 | 75 | 1.1309 | 1.2427 | 1.5561 |  | 1802.0821 | 1980.2283 | 2479.5892 | 4523.6198 | 4970.8058 | 6224.3107
26.6667 | 80 | 1.1092 | 1.2226 | 1.5132 |  | 1767.5305 | 1948.2256 | 2411.333 | 4436.888 | 4890.472 | 6052.973
29.4444 | 85 | 1.0872 | 1.2023 | 1.4694 |  | 1732.43 | 1915.7967 | 2341.4949 | 4348.778 | 4809.0685 | 5877.6639
32.2222 | 90 | 1.0648 | 1.1816 | 1.4245 |  | 1696.7511 | 1882.9226 | 2269.9489 | 4259.2161 | 4726.5473 | 5698.0679
35 | 95 | 1.042 | 1.1607 | 1.3785 |  | 1660.4616 | 1849.5828 | 2196.5514 | 4168.1215 | 4642.857 | 5513.8242
37.7778 | 100 | 1.0189 | 1.1395 | 1.3311 |  | 1623.5262 | 1815.7551 | 2121.137 | 4075.4055 | 4557.942 | 5324.5175
40.5556 | 105 | 0.99524 | 1.1179 | 1.2824 |  | 1585.9059 | 1781.4155 | 2043.5135 | 3980.9704 | 4471.7422 | 5129.6655
43.3333 | 110 | 0.97118 | 1.096 | 1.2322 |  | 1547.5577 | 1746.5379 | 1963.4557 | 3884.7081 | 4384.192 | 4928.7029
46.1111 | 115 | 0.94662 | 1.0738 | 1.1802 |  | 1508.4337 | 1711.0941 | 1880.6964 | 3786.4983 | 4295.2201 | 4720.9589
48.8889 | 120 | 0.92155 | 1.0512 | 1.1264 |  | 1468.4805 | 1675.0529 | 1794.9147 | 3686.207 | 4204.7488 | 4505.6281
51.6667 | 125 | 0.89592 | 1.0282 | 1.0704 |  | 1427.638 | 1638.3803 | 1705.7193 | 3583.6835 | 4112.6925 | 4281.7284
54.4444 | 130 | 0.86969 | 1.0047 | 1.012 |  | 1385.8386 | 1601.0388 | 1612.6249 | 3478.7577 | 4018.9574 | 4048.0409
57.2222 | 135 | 0.84281 | 0.98086 | 0.95076 |  | 1343.0051 | 1562.9873 | 1515.0159 | 3371.2364 | 3923.4397 | 3803.021
60 | 140 | 0.81522 | 0.95651 | 0.88617 |  | 1299.0497 | 1524.1797 | 1412.0922 | 3260.8986 | 3826.0242 | 3544.6601