## Offer Inputs
PSEG Proposed Fuel Cost Policy Process
Typical Input Parameters for a Dual Fuel-Fired Combined Cycle Unit
|  | Natural Gas | RTO Accepted | ULSD | RTO Accepted | RTO Comment
Fuel 1 Transportation Premium | $/MMBtu |  |  |  |  | Documentation required
Fuel 2 Transportation Premium | $/MMBtu |  |  |  |  | Documentation required
Cold Start-Up MMBtu | MMBtu |  |  |  |  | Approved
Cold Ramp-Up MMBtu | MMBtu |  |  |  |  | Preliminary estimate OK pending suppoprting documentation, outside of benchmark values.
Cold Start-Up Station Service | MWh |  |  |  |  | Preliminary estimate OK pending suppoprting documentation, outside of benchmark values.
Cold Start-Up VOM | $ |  |  |  |  | Approved
Intermediate Start-Up MMBtu | MMBtu |  |  |  |  | Approved
Intermediate Ramp-Up MMBtu | MMBtu |  |  |  |  | Approved
Intermediate Start-Up Station Service | MWh |  |  |  |  | Approved
Intermediate Start-Up VOM | $ |  |  |  |  | Approved
Hot Start-Up MMBtu | MMBtu |  |  |  |  | Approved
Hot Ramp-Up MMBtu | MMBtu |  |  |  |  | Preliminary estimate OK pending suppoprting documentation, outside of benchmark values.
Hot Start-Up Station Service | MWh |  |  |  |  | Preliminary estimate OK pending suppoprting documentation, outside of benchmark values.
Hot Start-Up VOM | $ |  |  |  |  | Approved
Ramp-Down MMBtu | MMBtu |  |  |  |  | Preliminary estimate OK pending suppoprting documentation
Shut-Down Station Service | MWh |  |  |  |  | Approved
No-Load VOM | $/hr |  |  |  |  | Approved
a0 Coefficient | non-negative constants |  |  |  |  | Approved
a1 Coefficient | non-negative constants |  |  |  |  | Approved
a2 Coefficient | non-negative constants |  |  |  |  | Approved
VOM | $/MWh |  |  |  |  | Approved
Emission Rate CO2 | lbs/MMBtu |  |  |  |  | Preliminary estimate OK pending suppoprting documentation. ISO Benchmark, 116.99 and 161.29 (gas/ULSD)
Emission Rate NOx | lbs/MMBtu |  |  |  |  | Approved
Emission Rate SO2 | lbs/MMBtu |  |  |  |  | Approved
Capacity Demand Rate | $/kVA
Capacity Demand value | kVA
Utility Rate Station Service | $/kW | Real Time | 0 | Real Time | 0
Opportunity Cost | ($/MWh)
Duct Fire or Upper Block | Text | Duct Fire/Peak |  | Duct Fire
Duct Fire Heat Rate | (MMBTu/MWh) |  |  |  |  | Approved
Duct Fire or Upper VOM | ($/MWh) |  |  |  |  | Approved
Duct Fire or Upper Block Begin MW | (MW) |  |  |  |  | Approved

## Time Based Parameters
Physical Operating Parameters
Parameters | Units | Participant Submitted value | IMM Approved | IMM Parameter Description
Minimum Run Time | Hours or fractions of hours |  |  | The minimum number of hours of operation at or above EcoMin that the generator owner requires the ISO recognize when committing the resource. The Minimum Run Time applies from the point where the generator is scheduled to be released for dispatch by the ISO from EcoMin, to the point where the ISO releases the generator for shut down from EcoMin.
Minimum Down Time | Hours or fractions of hours |  |  | The minimum number of hours that the generator owner requires between the time the generator is released for shutdown by the ISO and the time the generator is scheduled to be released for dispatch to the ISO.
Cold Start Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset connects to the grid at 0 MW, and the Generator is released for dispatch at the Economic Minimum Limit, from a Cold Start Condition.
Intermediate Start Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset connects to the grid at 0 MW, and the Generator is released for dispatch at the Economic Minimum Limit, from a Intermediate Start Condition.
Hot Start Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset connects to the grid at 0 MW, and the Generator is released for dispatch at the Economic Minimum Limit, from a Hot Start Condition.
Cold Notification Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset receives a start-up order from ISO, and when the Generator Asset connects to the grid at 0 MW, from a Cold operating condition.
Intermediate Notification Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset receives a start-up order from ISO, and when the Generator Asset connects to the grid at 0 MW, from a Intermediate operating condition.
Hot Notification Time | Hours or fractions of hours |  |  | The number of hours elapsed between when the Generator Asset receives a start-up order from ISO, and when the Generator Asset connects to the grid at 0 MW, from a Hot operating condition.
Hot to Cold Time | Hours or fractions of hours |  |  | The time from de-synchronization that cold conditions apply.
Hot to Intermediate Time | Hours or fractions of hours |  |  | The time from de-synchronization that intermediate conditions apply.
Cold Off Peak Notification | Hours or fractions of hours |  |  | See Cold Notification definition - Notification times, only applied in Off Peak hours that will replace the units normal Notification times. Peak hours are defined in New England as the week day hours between 0800 and 2300, excluding NERC holidays.
Intermediate Off Peak Notification | Hours or fractions of hours |  |  | See Intermediate Notification definition - Notification times, only applied in Off Peak hours that will replace the units normal Notification times. Peak hours are defined in New England as the week day hours between 0800 and 2300, excluding NERC holidays.
Hot Off Peak Notification | Hours or fractions of hours |  |  | See Hot Notification definition - Notification times, only applied in Off Peak hours that will replace the units normal Notification times. Peak hours are defined in New England as the week day hours between 0800 and 2300, excluding NERC holidays.
*Time Parameters do not change between natural gas operation and ULSD operation.
NOTE: These are definitions as used in ISO-NE - may not be applicable in PJM