## Setup
Enter Stakeholder Committee Name in cell A2:
Market Implementation Committee
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Co-Located Load Service

## 1. Interest Identification
Market Implementation Committee
Co-Located Load Service
Interest Identification
Instructions: List interests of all parties on this page.
Ensure System Reliability
1 | Ensure that reliability is not adversely impacted by any changes made to the status quo, and, ensure this is the case regardless of the total MW quantity of co-located load that might be added to the system.
4 | Sustainable general competitive definition of capacity
7 | Allow mechanism to preserve capacity in the market
13 | Prevent double counting of capacity or energy through this effort
Ensure Market Efficiency
2 | Ensure that any new processes, rules, requirements, etc. that are put in place to support any change to the status quo are transparent and robust.
3 | Ensure that any new processes, rules, requirements, etc. that are put in place do not create an uncompetitive market or incentivize uncompetitive market outcomes.
4 | Sustainable general competitive definition of capacity
6 | Enhance economic efficiency
Respect Regulatory Authority of States and Support State and Consumer Preferences
8 | Facilitate the location of these types of customers into PJM states
9 | Develop rules that allow these types of customers to locate into PJM states
10 | Respect state commission and RERRA regulatory authority
11 | Do not conflict with state laws
5 | Facilitate consumer choice
14 | Want to ensure visability of these resources to state commissions and EDCs
Ensure New Rules are Compatible With Other Compliance Efforts
12 | Avoid trumping or conflicting with PJM compliance efforts related to FERC Order 2222

## 2. Options Matrix- Design Comp.
Market Implementation Committee
Co-Located Load Service
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | Column1
* | Implementation
Scenario Set Up
A | Configurations |  | Two different configurations will be considered: Co-Located Load without Service from the System: The load is served exclusively by the co-located BTM generation and is disconnected whenever not being served by the BTM generation. Co-Located Load with Service from the System: The load is normally served by the co-located BTM generation but can be served from the system when not being served by the BTM generation.
B | Jurisdiction |  | Any modification made to a Generation Interconnection Customer’s facility, including the addition of co-located load, is premised on the Market Seller’s adherence with any and all applicable state and local rules for serving co-located behind the meter load.
Solution Components
C | Engineering
1 | Load Trip/Frequency Control |  | Following load trip, no special scheme in place to reduce generator output. Generator would reduce net output to achieve net MW basepoint under the generator existing control mode (AGC or manual dispatch).
2 | Generator Trip |  | Following generator trip, in one scenario, the load is curtailed automatically (net POI output never goes negative), and in the other, the load is not curtailed but instead supplied by the grid via the GSU (net POI output goes negative) or via a secondary feed from the system.
3 | RT Metering and Telemetry |  | MW/MVAR Metering (real-time quality only) required for significant sized loads >= 10 MW.
4 | Settlement Metering |  | Wholesale meter reflects output of generator net of BTML
5 | Reactive Modeling |  | Load needs to be modeled explicitly with MVAR metering to accurately assess reactive impact of the load at the POI. Generator and load modeled separately. Generator D-curve still based on physical reactive capability at generator terminals (not netted against the load).
6 | Contingency Modeling |  | Model separate generator and load contingencies to reflect reality (no netted generator/load contingency). Question about who will define the load contingency (PJM or the GO). Typically the TO reviews or supplies contingencies for PJM's analysis.
D | Market Design
7 | Capacity Market Must Offer Requirement |  | With the exception of Intermittent Resources and Capacity Storage Resources, all existing generation resources must offer available MW in each RPM Auction.
8 | Capacity Offer Development |  | A sell offer above $0 for an existing generation resource must seek unit-specifc exception request by submitting ACR data in accordance with section 6.8 of Attachment DD, or may utilize an offer cap based on default gross ACR if available.
9 | Capacity Accreditation |  | Capacity value of co-located generation is reduced by MW quantity of BTML. Reduction is applied to ICAP MW of thermal generation and to accredited UCAP MW of ELCC Resource.
10 | Energy Market Must Offer Requirement |  | A generator with a capacity commitment must submit a cost-based offer into the PJM DA and RT energy market each day (unless unavailable due to outage) in a MW quantity commensurate with the resource’s ICAP commitment level. A market-based offer submitted by such generator must also be in a MW quantity commensurate with it's ICAP commitment level. A Capacity Storage Resource or an Intermittent Resource may satisfy this energy market must offer requirement by either self-scheduling or offering the unit as a dispatchable resource where the hourly DA self-scheduled values may vary hour to hour from the capacity commitment.
11 | Cost-based Offer Development |  | Cost-based offers for energy from generating resources shall not exceed the variable cost of producing such energy as determined in accordance with Schedule 2.
12 | Market-based Offer Development |  | Market-based offers cannot exceed $1,000/MWh, except (1) when the cost-based offer is above $1,000/MWh and less than or equal to $2,000/MWh, then the market-based offer must be less than or equal to the cost-based offer; and (2) when the cost-based offer is greater than $2,000/MWh, then the market-based offer must be less than or equal to $2,000/MWh.
13 | Capacity Testing |  | Net Test Capacity equal to gross capability less station service/auxiliary load less co-located host/process load where gross capability and station service/auxiliary load are based on measurements made at time of each seasonal capacity verification test and co-located host/process load is based on the highest hourly MW quantity measured during the most recent 36 months at time of verification test.
14 | Response Time (how quickly load must be able to be interrupted) |  | N/A
15 | CIRs |  | CIRs are reduced by MW quantity of BTML.
16 | Load Interconnection (Planning) |  | The generation owner must notify PJM and the Interconnected TO of any modification to the generation facility, including the addition of co-located load, at least 90 days in advance of the beginning of physical construction so that PJM and the Interconnected TO can evaluate potential reliability impacts of the modification. The modification request will initiate the Necessary Study process.
17 | Load Forecasting |  | Load that is netted out by co-located BTM generation in any given hour is not included in the hourly PJM metered load for that hour. Historical hourly PJM metered load is used in developing the PJM peak load forecast therefore load that is normally netted out by operating BTM generation will not be reflected in the peak load forecast. The MW quantity of such load that is reflected in the peak load forecast is dependent upon historical hourly operation of the BTM generation as it relates to netting out the co-located load. | [6 empty] | Low
18 | Transmission Costs |  | PJM network load customers pay transmission-related costs based on their Network Service Peak Load ("NSPL"). The NSPL is determined by each EDC using EDC-specific procedures that, in general, base the NSPL on the customer load (net of operating BTMG) at the time of specific peak load hours. | [6 empty] | Low - Medium
19 | Distribution Costs |  | N/A
20 | Capacity Costs |  | LSEs pay capacity costs (i.e., RPM charges) based on their Peak Load Contribution ("PLC"). The PLC is determined by each EDC using EDC-specific procedures that, in general, base the PLC on the LSE's load (net of operating BTMG) at the time of specific peak load hours. | [6 empty] | Low - High
21 | Demand Response Eligibility |  | End-use customers may participate in RPM as DR in a MW quantity not to exceed the customer's Peak Load Contribution ("PLC"). | [6 empty] | Medium
22 | Curtailment Procedures |  | N/A | [6 empty] | Medium - High
23 | Settlements |  | Status Quo will be added if and when more specific settlement impacts are identified. | [6 empty] | High
24 | Treatment in PJM planning studies (e.g., Reserve, CETO, CETL, ELCC, Market Efficiency, etc.) |  | BTM co-located generation/load is not modeled separately in the Reserve Requirement Study model, the ELCC model or the Market Efficiency model. This is predominately the case with CETL & CETO, however, there are a small number of instances where the TO has separately reflected BTM co-located generation/load in the transmission planning power flow models that are ultimately used for CETL purposes. In these instances, the CETO model is updated to separately reflect this BTM generation/load for purpose of maintaining consistency between the two models.
25 | Amendments to ISA |  | The ISA or other relevant service agreement is amended to reduce CIRs to an amount equal to the generator's current CIRs less the capacity dedicated to the BTML (based on the highest expected hourly demand of the BTML). The MFO in the agreement may remain unchanged, provided the generator’s full output capability remains available to the system whenever the host load is offline. The ISA is also modified to reflect the facility modifications to incorporate the load (description of the load facility, updated one-line diagram in ISA Schedule B), as well as any additional required load metering (ISA Schedule C).
26 | Participation Caps |  | N/A | [6 empty] | Low - High
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
Market Implementation Committee
Co-Located Load Service
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component |  | Detailed Description
Scenario Set Up |  | The following rows describe the various scenarios that the solutions developed through this matrix will need to consider or accommodate. They will not be part of the package matrix. They are for informational purposes only.
A | Configurations | Describe interconnection relationship between transmission network, generator, and Behind the Meter Load (BTML)
B | Jurisdiction | Describe the jurisdiction responsible for the sale of power to the BTML and the conditions predicate for such jurisdiction
Solution Components |  | The following rows contain the design components that are expected to be part of the package matrix that is ultimately developed. Solution options will need to be offered for each of these rows.
C | Engineering | Header for the Engineering section of design components.
1 | Load Trip/Frequency Control | Describe the remedy for any new impacts to the grid as a consequence of the BTML tripping.
2 | Generator Trip | Describe remedy for any new impacts to the grid as a consequence of the generator tripping.
3 | RT Metering and Telemetry | Describe metering requirements for BTML, if needed.
4 | Settlement Metering | Describe settlement metering requirements for BTML, if needed.
5 | Reactive | Describe modeling and metering requirements to accurately assess reactive impact of BTML.
6 | Contingency Modeling | Describe impacts of BTML on contingency modeling.
D | Market Design | Header for the Market Design section of design components.
7 | Capacity Market Must Offer Requirement | Describe capacity must offer requirement obligation for the subject generator, including portion dedicated to BTML and portion that is not.
8 | Capacity Offer Development | Describe capacity offer distinctions, if any, for the portion dedicated to BTML and the portion that is not.
9 | Capacity Accreditation | Describe capacity accreditation impact of BTML
10 | Energy Market Must Offer Requirement | Describe DAM offer distinctions, if any, for the portion dedicated to BTML and the portion that is not.
11 | Cost-based Offer Development | Describe CBO distinctions, if any, for the portion dedicated to BTML and the portion that is not.
12 | Market-based Offer Development | Describe MBO distinctions, if any, for the portion dedicated to BTML and the portion that is not.
13 | Capacity Testing | Describe changes to capacity testing requirements, if any.
14 | Response Time (how quickly load must be able to be interrupted) | Describe how quickly must the load curtail to satisfy all engineering and market requirements.
15 | CIRs | Describe change to CIR retention rules, if any, for generator with co-located load.
16 | Load Interconnection (Planning) | Describe any required changes to load interconnection studies to accommodate the engineering and market requirements.
17 | Load Forecasting | Describe changes to PJM load forecasting (incl. add backs if necessary) and the conditions under which such changes are required.
18 | Transmission Costs | Describe any reforms to transmisison cost assessment.
19 | Distribution Costs | Describe any reforms to distribution cost assessment.
20 | Capacity costs | Describe any reforms to capacity cost assessment.
21 | Demand Response Eligibility | Describe conditions for BTML to participate in PJM DR programs.
22 | Curtailment Procedures | Describe engineering or market conditions that would require load curtailment. Describe responsible entity or entities.
23 | Settlements | Describe any settlements reforms required for the participating co-located generator or load.
24 | Treatment in PJM planning studies (e.g., Reserve, CETO, CETL, ELCC, Market Efficiency, etc.) | Do we need to make any changes to how we model or treat a resource with co-located load service in our studies?
25 | Amendments to ISA | Do we need new provision(s) in ISA to cover a resource with co-located load service?
26 | Participation Caps | Do we need some type of safety valve? Is there a point at which the proposed solution is no longer viable if too many existing generators choose to participate with co-located load service?

## 2b. Option Details
Market Implementation Committee
Co-Located Load Service
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Market Implementation Committee
Co-Located Load Service
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Market Implementation Committee
Co-Located Load Service
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Market Implementation Committee
Co-Located Load Service
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Market Implementation Committee
Co-Located Load Service
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1 | 2022-03-02 | Initial version.
2 | 2022-03-09 | Post-Meeting version. Additional Interest added.
3