## Tracking By Flowgate
2014 RTEP Proposal Window 2
Original Posting Date: 1/12/2015
Revised Posting Date: 2/4/2015
Version: 2
Revision History:
V1: Posted 1/12/2015
V2: Project 2014_2-2W status removed per January TEAC revision
*=Conductor Limited
Test | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | % Overload | Conductor Rating (MVA) | ContVolt | BaseVolt | Vdrop(%) | Low Limit | Upper Limit | Cont Type | Contingency 1 | Contingency 2 | Analysis Type/Case | Error Type | Violation Date | STATUS | Project ID | Upgrade/Greenfield | Proposing Entity | Cost ($M) | Target Zone
N-1-1 Thermal - Pratts | 1.1 | 314755 | 3GOLDALE | 314778 | 3PAY TAP | 1 | 115/115 | 345/345 | 226 | 107.26 | 110.4 | [8 empty] | 'LN 2088' | 'LN 2054' |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 2.1 | 314815 | 3OAK GRE | 314769 | 3ORANGE | 1 | 115/115 | 345/345 | 231 | 100.78 | 105.11 | [8 empty] | 'LN 2088' | 'LN 2054' |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 1.2 | 314755 | 3GOLDALE | 314778 | 3PAY TAP | 1 | 115/115 | 345/345 | 226 | 109.16 | 111.88 | [8 empty] | 'LN 2054' | 'LN 2088' |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 2.2 | 314815 | 3OAK GRE | 314769 | 3ORANGE | 1 | 115/115 | 345/345 | 231 | 100.69 | 104.97 | [8 empty] | 'LN 2054' | 'LN 2088' |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 1.3 | 314758 | 6GORDNVL | 314757 | 3GORDNVL | 2 | 230/115 | 345/345 | 250.9 | 127.42 | 128.29 | [8 empty] | 'LN 2135' | 'LN 255' |  |  |  | Removed From Window 2
N-1-1 Thermal - Pratts | 1.4 | 314758 | 6GORDNVL | 314757 | 3GORDNVL | 2 | 230/115 | 345/345 | 250.9 | 127.5 | 128.33 | [8 empty] | 'LN 255' | 'LN 2135' |  |  |  | Removed From Window 2
N-1-1 Thermal - Pratts | 1.5 | 314768 | 3MITCHEL | 314345 | 3MT RUN | 1 | 115/115 | 345/345 | 176 | 101.02 | 111.18 | [8 empty] | 'LN 6' | 'LN 2077' |  |  |  | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 1.6 | 314768 | 3MITCHEL | 314345 | 3MT RUN | 1 | 115/115 | 345/345 | 176 | 101.02 | 111.13 | [8 empty] | 'LN 2077' | 'LN 6' |  |  |  | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 2.6 | 314768 | 3MITCHEL | 314345 | 3MT RUN | 1 | 115/115 | 345/345 | 176 | 101.02 | 111.1 | [8 empty] | 'LN 2077' | '3REMNGCT-6REMNGCT' |  |  |  | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Thermal - Pratts | 1.7 | 314768 | 3MITCHEL | 314345 | 3MT RUN | 1 | 115/115 | 345/345 | 176 | 101.02 | 111.15 | [8 empty] | '3REMNGCT-6REMNGCT' | 'LN 2077' |  |  |  | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD49 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.7725 | 1.0037 | 23.12 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD50 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.7439 | 1.0009 | 25.7 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD51 | 314758 | 6GORDNVL |  |  |  | 230 | 345 | [5 empty] | 0.708 | 0.9636 | 25.56 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD52 | 314759 | 6HOLLYMD |  |  |  | 230 | 345 | [5 empty] | 0.7025 | 0.9735 | 27.1 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD53 | 314768 | 3MITCHEL |  |  |  | 115 | 345 | [5 empty] | 0.9058 | 1.0105 | 10.47 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD54 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.7974 | 1.0039 | 20.65 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD55 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.7558 | 1.0043 | 24.85 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD56 | 314815 | 3OAK GRE |  |  |  | 115 | 345 | [5 empty] | 0.9029 | 1.0157 | 11.28 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD57 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.7442 | 1.0014 | 25.72 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD58 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.6773 | 0.9368 | 25.95 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD59 | 314877 | 3OAK G_1 |  |  |  | 115 | 345 | [5 empty] | 0.9035 | 1.0164 | 11.29 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD60 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.7563 | 1.005 | 24.87 |  |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD61 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.7506 | 0.9368 | 18.62 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD62 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.8451 | 1.0037 | 15.86 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD63 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.8245 | 1.0009 | 17.64 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD64 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.862 | 1.0039 | 14.19 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD65 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.8338 | 1.0043 | 17.05 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD66 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.8249 | 1.0014 | 17.65 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD67 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.8343 | 1.005 | 17.07 |  |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD68 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.671 | 0.9378 | 26.68 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD69 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.7664 | 1.0016 | 23.52 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD70 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.737 | 1.0018 | 26.48 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD71 | 314758 | 6GORDNVL |  |  |  | 230 | 345 | [5 empty] | 0.7325 | 1.0081 | 27.56 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD72 | 314759 | 6HOLLYMD |  |  |  | 230 | 345 | [5 empty] | 0.7268 | 1.0033 | 27.65 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD73 | 314768 | 3MITCHEL |  |  |  | 115 | 345 | [5 empty] | 0.9028 | 1.0063 | 10.35 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD74 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.7919 | 1.0003 | 20.84 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD75 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.7491 | 1.004 | 25.49 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD76 | 314815 | 3OAK GRE |  |  |  | 115 | 345 | [5 empty] | 0.8997 | 1.0114 | 11.17 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD77 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.7373 | 1.0023 | 26.5 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD78 | 314877 | 3OAK G_1 |  |  |  | 115 | 345 | [5 empty] | 0.9003 | 1.0121 | 11.18 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD79 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.7496 | 1.0046 | 25.5 |  |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
N-1-1 Volt Drop - Pratts | N2-VD80 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.7504 | 0.9414 | 19.1 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD81 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.8446 | 1.0052 | 16.06 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD82 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.8241 | 1.0051 | 18.1 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD83 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.8614 | 1.004 | 14.26 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD84 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.8334 | 1.0074 | 17.4 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD85 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.8245 | 1.0056 | 18.11 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Drop - Pratts | N2-VD86 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.8339 | 1.0081 | 17.42 |  |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM3 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.7852 | 1.0037 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM4 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.7574 | 1.0009 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM5 | 314758 | 6GORDNVL |  |  |  | 230 | 345 | [5 empty] | 0.675 | 0.9636 |  | 0.9217 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM6 | 314759 | 6HOLLYMD |  |  |  | 230 | 345 | [5 empty] | 0.6698 | 0.9735 |  | 0.9217 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM7 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.8093 | 1.0039 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM8 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.769 | 1.0043 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM9 | 314815 | 3OAK GRE |  |  |  | 115 | 345 | [5 empty] | 0.9119 | 1.0157 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM10 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.6895 | 0.9368 |  | 0.9217 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM11 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.7577 | 1.0014 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM12 | 314877 | 3OAK G_1 |  |  |  | 115 | 345 | [5 empty] | 0.9125 | 1.0164 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM13 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.7695 | 1.005 |  | 0.913 |  |  | LN 2088 | LN 2054 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM14 | 235533 | 01PRATTS |  |  |  | 115 | 201 | [5 empty] | 0.7541 | 0.9368 |  | 0.9217 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM15 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.8487 | 1.0037 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM16 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.8281 | 1.0009 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM17 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.8656 | 1.0039 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM18 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.8374 | 1.0043 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM19 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.8286 | 1.0014 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM20 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.838 | 1.005 |  | 0.913 |  |  | LN 2088 | LN 2135 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM21 | 235533 | 01PRATTS |  |  |  | 115 | 345 | [5 empty] | 0.6891 | 0.9378 |  | 0.9217 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM22 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.785 | 1.0016 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM23 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.7571 | 1.0018 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM24 | 314758 | 6GORDNVL |  |  |  | 230 | 345 | [5 empty] | 0.675 | 1.0081 |  | 0.9217 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM25 | 314759 | 6HOLLYMD |  |  |  | 230 | 345 | [5 empty] | 0.6699 | 1.0033 |  | 0.9217 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM26 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.8091 | 1.0003 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM27 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.7688 | 1.004 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM28 | 314815 | 3OAK GRE |  |  |  | 115 | 345 | [5 empty] | 0.9117 | 1.0114 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM29 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.7575 | 1.0023 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM30 | 314877 | 3OAK G_1 |  |  |  | 115 | 345 | [5 empty] | 0.9124 | 1.0121 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM31 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.7693 | 1.0046 |  | 0.913 |  |  | LN 2054 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM32 | 235533 | 01PRATTS |  |  |  | 115 | 345 | [5 empty] | 0.7547 | 0.9414 |  | 0.9217 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM33 | 314756 | 3DOUBLDY |  |  |  | 115 | 345 | [5 empty] | 0.8491 | 1.0052 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM34 | 314757 | 3GORDNVL |  |  |  | 115 | 345 | [5 empty] | 0.8286 | 1.0051 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM35 | 314769 | 3ORANGE |  |  |  | 115 | 345 | [5 empty] | 0.866 | 1.004 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM36 | 314776 | 3SOMRSET |  |  |  | 115 | 345 | [5 empty] | 0.8379 | 1.0074 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM37 | 314875 | 3GORDN_1 |  |  |  | 115 | 345 | [5 empty] | 0.829 | 1.0056 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Volt Mag - Pratts | N2-VM38 | 314884 | 3SOMRS_1 |  |  |  | 115 | 345 | [5 empty] | 0.8385 | 1.0081 |  | 0.913 |  |  | LN 2135 | LN 2088 |  |  |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Non Conv - Pratts | N2-NC1 | [18 empty] | LN 255 | LN 2135 | Voltage Magnitude | Blown Up |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Non Conv - Pratts | N2-NC2 | [18 empty] | LN 2135 | LN 255 | Voltage Magnitude | Blown Up |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Non Conv - Pratts | N2-NC3 | [18 empty] | LN 2135 | LN 255 | Voltage Drop | Blown Up |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
N-1-1 Non Conv - Pratts | N2-NC4 | [18 empty] | LN 2054 | LN 255 | Voltage Drop | Blown Up |  | Removed From Window
N-1-1 Non Conv - Pratts | N2-NC5 | [18 empty] | LN 255 | LN 2054 | Voltage Drop | Blown Up |  | Removed From Window
N-1-1 Non Conv - Pratts | N2-NC6 | [18 empty] | LN 255 | LN 2135 | Voltage Drop | Blown Up |  | Pratts Area Analysis ongoing | 2014_2-6B | Greenfield | ITC Mid Atlantic | 142 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7D | Greenfield | Northeast Transmission Development | 93.1 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7E | Greenfield | Northeast Transmission Development | 60.9* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7F | Greenfield | Northeast Transmission Development | 109.9 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7G | Greenfield | Northeast Transmission Development | 77.7* | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7H | Greenfield | Northeast Transmission Development | 68.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7I | Greenfield | Northeast Transmission Development | 85.5 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7J | Greenfield | Northeast Transmission Development | 90.4 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-7K | Greenfield | Northeast Transmission Development | 107.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14A | Greenfield | Ameren | 139.35 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14B | Greenfield | Ameren | 169.23 | Dominion
[25 empty] | Pratts Area Analysis ongoing | 2014_2-14C | Greenfield | Ameren | 198.57 | Dominion
LL Gen Deliv | LL-1 | 272189 | OGLESBY ; T | 271987 | MAZON ; R | 1 | 138/138 | 222/222 | 115 | 180.85 | 174.43 |  | 173/223/230 | [5 empty] | single | '138-L0112__B-S' |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-8A | Upgrade | ComEd | 0.7 | Comed
[26 empty] | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-28 | 272367 | ROCK FALL; R | 272095 | NELSON ; R | 1 | 138/138 | 222/222 | 223 | 152.36 | 147.46 |  | 351/449/498 | [5 empty] | single | '187-L15508__' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8B | Upgrade | ComEd | 0.53 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-30 | 272367 | ROCK FALL; R | 272095 | NELSON ; R | 1 | 138/138 | 222/222 | 223 | 140.48 | 136.08 |  | 351/449/498 | [5 empty] | single | '138-L15508_R-R' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8B | Upgrade | ComEd | 0.53 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-34 | 272367 | ROCK FALL; R | 272095 | NELSON ; R | 1 | 138/138 | 222/222 | 173 | 108.18 | 104.56 |  | 351/449/498 | [5 empty] | single | Base Case |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8B | Upgrade | ComEd | 0.53 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-40 | 293510 | O09 OP1 138 | 272367 | ROCK FALL; R | 1 | 138/138 | 222/222 | 248 | 152.99 | 147.89 |  | 208/264/275* | [5 empty] | single | '187-L15508__' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8C | Upgrade | ComEd | 10.5 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-42 | 293510 | O09 OP1 138 | 272367 | ROCK FALL; R | 1 | 138/138 | 222/222 | 248 | 144.96 | 140.34 |  | 208/264/275* | [5 empty] | single | '138-L15508_R-R' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8C | Upgrade | ComEd | 10.5 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-45 | 293510 | O09 OP1 138 | 272367 | ROCK FALL; R | 1 | 138/138 | 222/222 | 208 | 107.65 | 103.88 |  | 208/264/275 | [5 empty] | single | Base Case |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8C | Upgrade | ComEd | 10.5 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-61 | 293710 | O29 | 272097 | NELSON ;RT | 1 | 138/138 | 222/222 | 264 | 143.38 | 138.58 |  | 208/248/275* | [5 empty] | single | '133-CB_23___' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8D | Upgrade | ComEd | 12.2 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-63 | 293710 | O29 | 272097 | NELSON ;RT | 1 | 138/138 | 222/222 | 264 | 140.27 | 135.82 |  | 208/248/275* | [5 empty] | single | '138-L15509GR-R' |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8D | Upgrade | ComEd | 12.2 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-69 | 293710 | O29 | 272097 | NELSON ;RT | 1 | 138/138 | 222/222 | 208 | 109.84 | 106.48 |  | 208/248/275 | [5 empty] | single | Base Case |  |  |  |  | FSA evaluation is in progress | 2014_2-7C | Greenfield | Northeast Transmission Development | 33.7 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8D | Upgrade | ComEd | 12.2 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-8E | Greenfield | ComEd | 16.1 | Comed
[25 empty] | FSA evaluation is in progress | 2014_2-12A | Greenfield | NIPSCO | 450 | Comed/MISO
LL Gen Deliv | LL-116 | 242512 | 05CLOVRD | 242524 | 05CLOVRD | 10 | 765/345 | 205/205 | 1587 | 104.1 | 104.93 | [7 empty] | single | '7421_B3_05CLOVRD 765-1'
LL N-1 Volt Mag | LL-V1 | 200942 | 26PIERCEBRK |  |  |  | 345 | 226 | [5 empty] | 1.0509 | 1.0398 |  |  | 1.0493 | Single | B_PN345-SX-#7_C |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V2 | 200942 | 26PIERCEBRK |  |  |  | 345 | 226 | [5 empty] | 1.0538 | 1.0398 |  |  | 1.0493 | Single | B_PN230-SX-#26A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V3 | 200942 | 26PIERCEBRK |  |  |  | 345 | 226 | [5 empty] | 1.0612 | 1.0398 |  |  | 1.0493 | Single | B_PN230-LS-#29A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V4 | 200942 | 26PIERCEBRK |  |  |  | 345 | 226 | [5 empty] | 1.0614 | 1.0398 |  |  | 1.0493 | Single | LEWIS RN _ FARM VLY _0730_A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V5 | 200942 | 26PIERCEBRK |  |  |  | 345 | 226 | [5 empty] | 1.0767 | 1.0398 |  |  | 1.0493 | Single | FARM_V_345_FARM_V_230A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V6 | 219750 | MERCER_6 |  |  |  | 230 | 231 | [5 empty] | 1.0957 | 1.0298 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V7 | 219749 | MERCER_5 |  |  |  | 230 | 231 | [5 empty] | 1.0956 | 1.0298 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V8 | 219748 | MERCER_4 |  |  |  | 230 | 231 | [5 empty] | 1.0956 | 1.0298 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V9 | 219747 | MERCER_3 |  |  |  | 230 | 231 | [5 empty] | 1.0956 | 1.0298 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V10 | 219746 | MERCER_1 |  |  |  | 230 | 231 | [5 empty] | 1.0957 | 1.0298 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V11 | 219147 | KUSER_H |  |  |  | 230 | 231 | [5 empty] | 1.094 | 1.0308 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V12 | 219119 | TRENTON_H |  |  |  | 230 | 231 | [5 empty] | 1.0936 | 1.0314 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V13 | 219118 | TRENTON_B |  |  |  | 230 | 231 | [5 empty] | 1.0945 | 1.0316 |  |  | 1.0522 | Single | L_A-2201 | [5 empty] | 2014_2-5A | Greenfield | PECO | 20.5 | PSEG
[26 empty] | 2014_2-5B | Greenfield | PECO | 35.5 | PSEG
[26 empty] | 2014_2-6A | Greenfield | ITC Mid Atlantic | 56-97 | PSEG
[26 empty] | 2014_2-11B | Upgrade | PSEG | 47 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11D | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11E | Upgrade | PSEG | 7.2 | PSEG
[26 empty] | 2014_2-11F | Upgrade | PSEG | 13.4 | PSEG
LL N-1 Volt Mag | LL-V14 | 200943 | 26PIERCEBRK |  |  |  | 230 | 226 | [5 empty] | 1.0591 | 1.0359 |  |  | 1.05 | Single | B_PN230-LS-#29A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V15 | 200943 | 26PIERCEBRK |  |  |  | 230 | 226 | [5 empty] | 1.0592 | 1.0359 |  |  | 1.05 | Single | LEWIS RN _ FARM VLY _0730_A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V16 | 200857 | 26MARSHALL |  |  |  | 230 | 226 | [5 empty] | 1.0516 | 1.0356 |  |  | 1.05 | Single | B_PN230-SX-#7A |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V17 | 342799 | 5S OAKHILL |  |  |  | 161 | 320 | [5 empty] | 1.0525 | 1.0506 |  |  | 1.05 | Single | EKPC CIRCUIT COOPER TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V18 | 342799 | 5S OAKHILL |  |  |  | 161 | 320 | [5 empty] | 1.0529 | 1.0506 |  |  | 1.05 | Single | EKPC CIRCUIT LAUREL CO TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V19 | 342799 | 5S OAKHILL |  |  |  | 161 | 320 | [5 empty] | 1.0535 | 1.0506 |  |  | 1.05 | Single | EKPC LINE RUSSELL CO JCT-WOLF CREEK 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V20 | 342790 | 5PULASK CO J |  |  |  | 161 | 320 | [5 empty] | 1.0509 | 1.0469 |  |  | 1.05 | Single | EKPC LINE CASEY CO-LIBERTY JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V21 | 342790 | 5PULASK CO J |  |  |  | 161 | 320 | [5 empty] | 1.0513 | 1.0469 |  |  | 1.05 | Single | EKPC CIRCUIT LIBERTY JCT TO MARION CO 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V22 | 342790 | 5PULASK CO J |  |  |  | 161 | 320 | [5 empty] | 1.0521 | 1.0469 |  |  | 1.05 | Single | EKPC LINE CASEY CO-MARION CO 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V23 | 342790 | 5PULASK CO J |  |  |  | 161 | 320 | [5 empty] | 1.0542 | 1.0469 |  |  | 1.05 | Single | EKPC LINE LIBERTY JCT-PULASKI JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V24 | 342787 | 5PULASK CO |  |  |  | 161 | 320 | [5 empty] | 1.0503 | 1.0465 |  |  | 1.05 | Single | EKPC LINE CASEY CO-LIBERTY JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V25 | 342787 | 5PULASK CO |  |  |  | 161 | 320 | [5 empty] | 1.0507 | 1.0465 |  |  | 1.05 | Single | EKPC CIRCUIT LIBERTY JCT TO MARION CO 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V26 | 342787 | 5PULASK CO |  |  |  | 161 | 320 | [5 empty] | 1.0515 | 1.0465 |  |  | 1.05 | Single | EKPC LINE CASEY CO-MARION CO 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V27 | 342787 | 5PULASK CO |  |  |  | 161 | 320 | [5 empty] | 1.0535 | 1.0465 |  |  | 1.05 | Single | EKPC LINE LIBERTY JCT-PULASKI JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V28 | 342745 | 5JABEZ T |  |  |  | 161 | 320 | [5 empty] | 1.0504 | 1.045 |  |  | 1.05 | Single | EKPC LINE RUSSELL CO JCT-WOLF CREEK 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V29 | 342727 | 5DENNY |  |  |  | 161 | 320 | [5 empty] | 1.0529 | 1.0511 |  |  | 1.05 | Single | EKPC LINE LIBERTY JCT-PULASKI JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V30 | 342727 | 5DENNY |  |  |  | 161 | 320 | [5 empty] | 1.0529 | 1.0511 |  |  | 1.05 | Single | EKPC CIRCUIT COOPER TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V31 | 342727 | 5DENNY |  |  |  | 161 | 320 | [5 empty] | 1.0529 | 1.0511 |  |  | 1.05 | Single | EKPC LINE JAMESTOWN JCT-RUSSELL CO JCT 161 KV-6-6-6-5 |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V32 | 342727 | 5DENNY |  |  |  | 161 | 320 | [5 empty] | 1.0533 | 1.0511 |  |  | 1.05 | Single | EKPC CIRCUIT LAUREL CO TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V33 | 342727 | 5DENNY |  |  |  | 161 | 320 | [5 empty] | 1.0538 | 1.0511 |  |  | 1.05 | Single | EKPC BREAKER COOPER BUS#1-COOPER BUS #2 161 K-20-14-14 |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V34 | 342718 | 5COOPER2 |  |  |  | 161 | 320 | [5 empty] | 1.0553 | 1.0533 |  |  | 1.05 | Single | EKPC CIRCUIT COOPER TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V35 | 342718 | 5COOPER2 |  |  |  | 161 | 320 | [5 empty] | 1.0553 | 1.0533 |  |  | 1.05 | Single | EKPC LINE LIBERTY JCT-PULASKI JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V36 | 342718 | 5COOPER2 |  |  |  | 161 | 320 | [5 empty] | 1.0556 | 1.0533 |  |  | 1.05 | Single | EKPC LINE JAMESTOWN JCT-RUSSELL CO JCT 161 KV-6-6-6-5 |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V37 | 342718 | 5COOPER2 |  |  |  | 161 | 320 | [5 empty] | 1.0557 | 1.0533 |  |  | 1.05 | Single | EKPC CIRCUIT LAUREL CO TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V38 | 342718 | 5COOPER2 |  |  |  | 161 | 320 | [5 empty] | 1.0567 | 1.0533 |  |  | 1.05 | Single | EKPC BREAKER COOPER BUS#1-COOPER BUS #2 161 K-20-14-14 |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V39 | 342715 | 5COOPER1 |  |  |  | 161 | 320 | [5 empty] | 1.0552 | 1.0532 |  |  | 1.05 | Single | EKPC LINE COOPER TO SOUTH OAKHILL JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V40 | 342715 | 5COOPER1 |  |  |  | 161 | 320 | [5 empty] | 1.0552 | 1.0532 |  |  | 1.05 | Single | EKPC CIRCUIT COOPER TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V41 | 342715 | 5COOPER1 |  |  |  | 161 | 320 | [5 empty] | 1.0553 | 1.0532 |  |  | 1.05 | Single | EKPC LINE LIBERTY JCT-PULASKI JCT 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V42 | 342715 | 5COOPER1 |  |  |  | 161 | 320 | [5 empty] | 1.0556 | 1.0532 |  |  | 1.05 | Single | EKPC LINE JAMESTOWN JCT-RUSSELL CO JCT 161 KV-6-6-6-5 |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V43 | 342715 | 5COOPER1 |  |  |  | 161 | 320 | [5 empty] | 1.0557 | 1.0532 |  |  | 1.05 | Single | EKPC CIRCUIT LAUREL CO TO LAUREL DAM 161 KV |  |  |  |  | Case Update, Invalid Violation | 2014_2-9D | Upgrade | EKPC | N/A | EKPC
LL N-1 Volt Mag | LL-V44 | 200944 | 26PIERCEBRK |  |  |  | 115 | 226 | [5 empty] | 1.0562 | 1.0379 |  |  | 1.05 | Single | LEWIS RN _ FARM VLY _0730_A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V45 | 200944 | 26PIERCEBRK |  |  |  | 115 | 226 | [5 empty] | 1.0564 | 1.0379 |  |  | 1.05 | Single | B_PN230-LS-#29A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V46 | 200856 | 26LICK RUN |  |  |  | 115 | 226 | [5 empty] | 1.0674 | 1.0432 |  |  | 1.05 | Single | B_PN115-LX-#198 |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V47 | 200803 | 26MEY.NORT |  |  |  | 115 | 226 | [5 empty] | 1.0684 | 1.0442 |  |  | 1.05 | Single | B_PN115-LX-#198 |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V48 | 200761 | 26ARNOLD R |  |  |  | 115 | 226 | [5 empty] | 1.0679 | 1.0437 |  |  | 1.05 | Single | B_PN115-LX-#198 |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V49 | 200747 | 26PENN-MAR |  |  |  | 115 | 226 | [5 empty] | 1.0554 | 1.0414 |  |  | 1.05 | Single | B_PN115-LX-#198 |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V50 | 200746 | 26ROCKWOOD |  |  |  | 115 | 226 | [5 empty] | 1.0644 | 1.0401 |  |  | 1.05 | Single | B_PN115-LX-#198 |  |  |  |  | Removed from Window 2
LL N-1 Volt Mag | LL-V51 | 200668 | 26FARM VLY |  |  |  | 115 | 226 | [5 empty] | 1.054 | 1.0376 |  |  | 1.05 | Single | LEWIS RN _ FARM VLY _0730_A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V52 | 200668 | 26FARM VLY |  |  |  | 115 | 226 | [5 empty] | 1.0543 | 1.0376 |  |  | 1.05 | Single | B_PN230-LS-#29A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V53 | 200663 | 26TWOMILE |  |  |  | 115 | 226 | [5 empty] | 1.0508 | 1.0347 |  |  | 1.05 | Single | LEWIS RN _ FARM VLY _0730_A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
LL N-1 Volt Mag | LL-V54 | 200663 | 26TWOMILE |  |  |  | 115 | 226 | [5 empty] | 1.0511 | 1.0347 |  |  | 1.05 | Single | B_PN230-LS-#29A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4A | Upgrade | First Energy | 5.53 | Penelec
N-1 Volt Mag | N1-VM1 | 235131 | 01BRACKENRDG |  |  |  | 138 | 201 | [5 empty] | 0.9185 | 0.9821 |  | 0.92 |  | Line_FB | AP_SB_352A |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4B | Upgrade | First Energy | 0.93 | APS
N-1 Volt Drop | N1-VD1 | 342634 | 4PLUMVILLE |  |  |  | 138 | 320 | [5 empty] | 0.902 | 1.0104 | 10.84 |  |  | Tower | TOWER_7 |  |  |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-9B | Upgrade | EKPC | 0.76 | EKPC
N-1 Volt Drop | N1-VD2 | 235971 | 01SQUABHLLW |  |  |  | 230 | 201 | [5 empty] | 0.939 | 1.02 | 8.1 |  |  | Line_FB | C2-AP-230-SQUAB1 |  |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD1 | 204615 | 27GLENDON |  |  |  | 115 | 227 | [5 empty] | 0.8894 | 0.9991 | 10.97 |  |  |  | PL100148A | B_ME115-SX-#35 |  |  |  |  | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4C | Upgrade | First Energy | 0.98 | Meted
N-1-1 Volt Drop | N2-VD2 | 204520 | 27ALLEN |  |  |  | 115 | 227 | [5 empty] | 0.8659 | 1.0142 | 14.83 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD3 | 204526 | 27DILLSBRG |  |  |  | 115 | 227 | [5 empty] | 0.867 | 1.0152 | 14.82 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD4 | 204528 | 27GARDNERS |  |  |  | 115 | 227 | [5 empty] | 0.8722 | 1.0165 | 14.43 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD5 | 204546 | 27MOUNTAIN |  |  |  | 115 | 227 | [5 empty] | 0.8676 | 1.0145 | 14.69 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD6 | 204552 | 27P.P.G.I. |  |  |  | 115 | 227 | [5 empty] | 0.867 | 1.0141 | 14.71 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD7 | 204556 | 27ROUND TP |  |  |  | 115 | 227 | [5 empty] | 0.8675 | 1.0167 | 14.92 |  |  |  | B_ME115-SX-#28 | B_ME115-SX-#6 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD8 | 204615 | 27GLENDON |  |  |  | 115 | 227 | [5 empty] | 0.8886 | 0.9975 | 10.89 |  |  |  | B_ME115-SX-#35 | PL100148A |  |  |  |  | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4C | Upgrade | First Energy | 0.98 | Meted
N-1-1 Volt Drop | N2-VD9 | 204520 | 27ALLEN |  |  |  | 115 | 227 | [5 empty] | 0.8652 | 0.9907 | 12.55 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD10 | 204526 | 27DILLSBRG |  |  |  | 115 | 227 | [5 empty] | 0.8664 | 0.9911 | 12.47 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD11 | 204528 | 27GARDNERS |  |  |  | 115 | 227 | [5 empty] | 0.8716 | 0.9914 | 11.98 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD12 | 204546 | 27MOUNTAIN |  |  |  | 115 | 227 | [5 empty] | 0.867 | 0.9912 | 12.42 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD13 | 204552 | 27P.P.G.I. |  |  |  | 115 | 227 | [5 empty] | 0.8664 | 0.9908 | 12.44 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD14 | 204556 | 27ROUND TP |  |  |  | 115 | 227 | [5 empty] | 0.8668 | 0.9931 | 12.63 |  |  |  | B_ME115-SX-#6 | B_ME115-SX-#28 |  |  |  | Still evaluating the upgrades due to assumption changes in the area | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4D | Upgrade | First Energy | 0.96 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-4E | Greenfield | First Energy | 19.33 | Meted
[25 empty] | Still evaluating the upgrades due to assumption changes in the area | 2014_2-7B | Greenfield | Northeast Transmission Development | 22 | Meted
N-1-1 Volt Drop | N2-VD15 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.9557 | 1.0061 | 5.04 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD16 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.945 | 1.0061 | 6.11 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD17 | 218335 | LAFAYET_M |  |  |  | 230 | 231 | [5 empty] | 0.9471 | 1.0043 | 5.72 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD18 | 218336 | LAFAYET_V |  |  |  | 230 | 231 | [5 empty] | 0.9472 | 1.0041 | 5.69 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD19 | 218341 | WDBRDG_V |  |  |  | 230 | 231 | [5 empty] | 0.9463 | 1.0049 | 5.86 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD20 | 218355 | NEWDOVR_H |  |  |  | 230 | 231 | [5 empty] | 0.9472 | 1.0025 | 5.53 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD21 | 218357 | PRSNAVS_H |  |  |  | 230 | 231 | [5 empty] | 0.9482 | 1.0038 | 5.56 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD22 | 218358 | PRSNAVS_S |  |  |  | 230 | 231 | [5 empty] | 0.9485 | 1.0039 | 5.54 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD23 | 218367 | WDBRDG_M |  |  |  | 230 | 231 | [5 empty] | 0.946 | 1.0048 | 5.88 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD24 | 218368 | WDBRDG_X |  |  |  | 230 | 231 | [5 empty] | 0.9453 | 1.0045 | 5.92 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD25 | 218469 | METUCHEN |  |  |  | 230 | 231 | [5 empty] | 0.9483 | 1.0039 | 5.56 |  |  |  | L_I-2287_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD26 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.9553 | 1.006 | 5.07 |  |  |  | L_I-2287 | L_R-2218 |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD27 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.9444 | 1.006 | 6.16 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD28 | 218335 | LAFAYET_M |  |  |  | 230 | 231 | [5 empty] | 0.9465 | 1.0042 | 5.77 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD29 | 218336 | LAFAYET_V |  |  |  | 230 | 231 | [5 empty] | 0.9466 | 1.0039 | 5.73 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD30 | 218341 | WDBRDG_V |  |  |  | 230 | 231 | [5 empty] | 0.9457 | 1.0048 | 5.91 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD31 | 218355 | NEWDOVR_H |  |  |  | 230 | 231 | [5 empty] | 0.9465 | 1.0023 | 5.58 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD32 | 218357 | PRSNAVS_H |  |  |  | 230 | 231 | [5 empty] | 0.9476 | 1.0036 | 5.6 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD33 | 218358 | PRSNAVS_S |  |  |  | 230 | 231 | [5 empty] | 0.948 | 1.0038 | 5.58 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD34 | 218367 | WDBRDG_M |  |  |  | 230 | 231 | [5 empty] | 0.9454 | 1.0047 | 5.93 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD35 | 218368 | WDBRDG_X |  |  |  | 230 | 231 | [5 empty] | 0.9447 | 1.0044 | 5.97 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD36 | 218469 | METUCHEN |  |  |  | 230 | 231 | [5 empty] | 0.9478 | 1.0038 | 5.6 |  |  |  | L_I-2287 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD37 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.9592 | 1.0097 | 5.05 |  |  |  | L_H-2286 | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD38 | 218311 | SEWAREN |  |  |  | 230 | 231 | [5 empty] | 0.9543 | 1.0074 | 5.31 |  |  |  | L_S-2219_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD39 | 218341 | WDBRDG_V |  |  |  | 230 | 231 | [5 empty] | 0.9557 | 1.0065 | 5.08 |  |  |  | L_S-2219_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD40 | 218367 | WDBRDG_M |  |  |  | 230 | 231 | [5 empty] | 0.9553 | 1.0063 | 5.1 |  |  |  | L_S-2219_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD41 | 218368 | WDBRDG_X |  |  |  | 230 | 231 | [5 empty] | 0.9546 | 1.0061 | 5.15 |  |  |  | L_S-2219_LT | L_R-2218_LT |  |  |  |  | 2014_2-3B | Greenfield | Transource | 13.6 | PSEG
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-11A | Upgrade | PSEG | 8.4 | PSEG
[26 empty] | 2014_2-11C | Upgrade | PSEG | 71 | PSEG
N-1-1 Volt Drop | N2-VD42 | 235268 | 01WASH |  |  |  | 138 | 201 | [5 empty] | 0.8552 | 0.9573 | 10.21 |  |  |  | 'AP_B2_518' | 'APS_B_G213' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD43 | 235182 | 01FRANKL |  |  |  | 138 | 201 | [5 empty] | 0.8435 | 0.9485 | 10.5 |  |  |  | 'AP_B2_518' | 'AP_FRANKLIN-WHITELEYA' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD44 | 235182 | 01FRANKL |  |  |  | 138 | 201 | [5 empty] | 0.8484 | 0.9492 | 10.08 |  |  |  | 'APS_B_G199' | 'AP_FRANKLIN-WHITELEYA' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD45 | 235261 | 01VANCEV |  |  |  | 138 | 201 | [5 empty] | 0.8717 | 0.9859 | 11.42 |  |  |  | 'APS_B_G213' | 'APS_B_G199' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD46 | 235268 | 01WASH |  |  |  | 138 | 201 | [5 empty] | 0.8698 | 0.9737 | 10.39 |  |  |  | 'APS_B_G213' | 'APS_B_G199' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD47 | 235455 | 01DAMASC |  |  |  | 230 | 201 | [5 empty] | 0.9276 | 1.0079 | 8.03 |  |  |  | 'APS_B_G580' | 'APS_B_G562' |  |  |  | Removed from Window 2
N-1-1 Volt Drop | N2-VD48 | 342634 | 4PLUMVILLE |  |  |  | 138 | 320 | [5 empty] | 0.8997 | 1.0061 | 10.64 |  |  |  | 'EC GODDARD-SPURLOCK 138 KV' | 'EL SPURLOCK TO MAYSVILLE JCT 138 KV' |  |  |  | Case Update, Invalid Violation | 2014_2-9C | Upgrade | EKPC | N/A | EKPC
N-1-1 Volt Mag | N2-VM1 | 204615 | 27GLENDON |  |  |  | 115 | 227 | [5 empty] | 0.9008 | 0.9991 |  | 0.9217 |  |  | PL100148A | B_ME115-SX-#35 |  |  |  |  | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4C | Upgrade | First Energy | 0.98 | Meted
N-1-1 Volt Mag | N2-VM2 | 204615 | 27GLENDON |  |  |  | 115 | 227 | [5 empty] | 0.8989 | 0.9975 |  | 0.9217 |  |  | B_ME115-SX-#35 | PL100148A |  |  |  |  | 2014_2-3A | Greenfield | Transource | 16.13 | Meted
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4C | Upgrade | First Energy | 0.98 | Meted
AEP Thermal TO Criteria | AEP-T1 | 244696 | CONNORST | 244705 | E HUNTGT | 1 | 34.5/34.5 | 205 | 21 |  |  | 246.8 | 56 | [6 empty] | 5877_B2_TOR186 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T2 | 244696 | CONNORST | 244705 | E HUNTGT | 1 | 34.5/34.5 | 205 | 21 |  |  | 244.52 | 56 | [6 empty] | 1267_B3_05NPROCT 765-1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T3 | 244696 | CONNORST | 244705 | E HUNTGT | 1 | 34.5/34.5 | 205 | 21 |  |  | 242.43 | 56 | [6 empty] | 05W HUNT-W.HUNTEQ |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T4 | 244696 | CONNORST | 244705 | E HUNTGT | 1 | 34.5/34.5 | 205 | 21 |  |  | 242.2 | 56 | [6 empty] | 6035_B2_TOR149 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T5 | 244696 | CONNORST | 244705 | E HUNTGT | 1 | 34.5/34.5 | 205 | 21 |  |  | 241.51 | 56 | [6 empty] | 5875_B2_TOR185A_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T6 | 244822 | SLAUGHTR | 244823 | WINIFRED | 1 | 46/46 | 205 | 27 |  |  | 127.29 | 27* | [6 empty] | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Thermal TO Criteria | AEP-T7 | 244822 | SLAUGHTR | 244823 | WINIFRED | 1 | 46/46 | 205 | 27 |  |  | 126 | 27* | [6 empty] | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Thermal TO Criteria | AEP-T8 | 244471 | BECCO | 244481 | LATROBE | 1 | 46/46 | 205 | 23 |  |  | 123.67 | 23* | [6 empty] | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T9 | 242644 | 05FREMO1 | 242873 | FREMONT- | 1 | 69/138 | 205 | 59 |  |  | 122.89 | 67* | [6 empty] | 5957_B2_TOR176_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2I | Upgrade | AEP | 2.5 | AEP
AEP Thermal TO Criteria | AEP-T10 | 244740 | 23RD ST | 244741 | 24TH ST | 1 | 34.5/34.5 | 205 | 27 |  |  | 122.41 | 27* | [6 empty] | 5877_B2_TOR186 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2J | Upgrade | AEP | 12.56 | AEP
AEP Thermal TO Criteria | AEP-T11 | 244471 | BECCO | 244481 | LATROBE | 1 | 46/46 | 205 | 23 |  |  | 121.1 | 23* | [6 empty] | 8757_B2 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T12 | 244471 | BECCO | 244481 | LATROBE | 1 | 46/46 | 205 | 23 |  |  | 115.03 | 23* | [6 empty] | 8762_B3_05SUNDL2 138- |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T13 | 244238 | HAYSI SS | 244248 | MOSS | 1 | 69/69 | 205 | 50 |  |  | 110.46 | 50* | [6 empty] | 5295_B2_TOR97A_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2B | Upgrade | AEP | 31.86 | AEP
AEP Thermal TO Criteria | AEP-T14 | 244480 | CHAUNCEY | 244509 | PINE GAP | 1 | 46/46 | 205 | 22 |  |  | 106.69 | 34 | [6 empty] | 8759_B2 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2O | Upgrade | AEP | N/A | AEP
AEP Thermal TO Criteria | AEP-T15 | 244471 | BECCO | 244481 | LATROBE | 1 | 46/46 | 205 | 23 |  |  | 106.38 | 23* | [6 empty] | 5356_B2_TOR12638 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T16 | 244471 | BECCO | 244481 | LATROBE | 1 | 46/46 | 205 | 23 |  |  | 106.26 | 23* | [6 empty] | 8761_B2_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T17 | 243948 | BRANTLY | 243949 | BRIDGE S | 1 | 69/69 | 205 | 105 |  |  | 105.02 | 100* | [6 empty] | 5424_B2_TOR107 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2A | Upgrade | AEP | 1.5 | AEP
AEP Thermal TO Criteria | AEP-T18 | 244828 | CLENDENI | 244833 | HARTLAND | 1 | 46/46 | 205 | 27 |  |  | 104.12 | 27* | [6 empty] | 5342_B2_TOR2371A_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 |  | 2014_2-2Q | Greenfield | AEP | 75.5 | AEP
[26 empty] | 2014_2-2R | Greenfield | AEP | 57.5 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2S | Greenfield | AEP | 53 | AEP
AEP Thermal TO Criteria | AEP-T19 | 244237 | HAYSI | 244598 | ELKHRNCT | 1 | 69/69 | 205 | 35 |  |  | 103.82 | 35* | [6 empty] | 5973_B2_TOR2332 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2B | Upgrade | AEP | 31.86 | AEP
AEP Thermal TO Criteria | AEP-T20 | 244899 | SCARBRO | 247334 | PAX BR | 1 | 46/46 | 205 | 27 |  |  | 102.97 | 27* | [6 empty] | 8765_B2_TOR74A_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2T | Upgrade | AEP | 11.3 | AEP
AEP Thermal TO Criteria | AEP-T21 | 244305 | RICHLNDS | 244315 | TOWNOF R | 1 | 69/69 | 205 | 74 |  |  | 102.54 | 102 | [6 empty] | 8451_B2 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2P | Upgrade | AEP | 0.2 | AEP
AEP Thermal TO Criteria | AEP-T22 | 244828 | CLENDENI | 244833 | HARTLAND | 1 | 46/46 | 205 | 27 |  |  | 102.48 | 27* | [6 empty] | 5343_B2_TOR2371B_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 |  | 2014_2-2Q | Greenfield | AEP | 75.5 | AEP
[26 empty] | 2014_2-2R | Greenfield | AEP | 57.5 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2S | Greenfield | AEP | 53 | AEP
AEP Thermal TO Criteria | AEP-T23 | 244228 | CLINTWTP | 244244 | LICKFKTP | 1 | 69/69 | 205 | 50 |  |  | 101.94 | 50* | [6 empty] | 7171_B2_TOR177C_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2H | Upgrade | AEP | 14.5 | AEP
AEP Thermal TO Criteria | AEP-T24 | 244822 | SLAUGHTR | 244823 | WINIFRED | 1 | 46/46 | 205 | 27 |  |  | 100.7 | 27* | [6 empty] | 5301_B2_TOR118D_MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Thermal TO Criteria | AEP-T25 | 244516 | SKINFORK | 244526 | THREEFRK | 1 | 46/46 | 205 | 29 |  |  | 100.29 | 29* | [6 empty] | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Thermal TO Criteria | AEP-T26 | 244228 | CLINTWTP | 244244 | LICKFKTP | 1 | 69/69 | 205 | 50 |  |  | 100.15 | 50* | [6 empty] | 8333_B2_TOR8880_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2H | Upgrade | AEP | 14.5 | AEP
AEP Thermal TO Criteria | AEP-T27 | 246329 | KANKAKEE | 246363 | TORNGT Z | 1 | 34.5/34.5 | 205 | 27 |  |  | 127.87 | 27* | [6 empty] | B3_Jackson Road 138/34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2 |  | #N/A | #N/A | #N/A | #N/A
AEP Thermal TO Criteria | AEP-T28 | 246340 | LYDICK | 246369 | W SIDE | 1 | 34.5/34.5 | 205 | 27 |  |  | 120.76 | 27* | [6 empty] | B3_New Carlisle 138/34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 |  | 2014_2-2C | Upgrade | AEP | 8.778 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2D | Upgrade | AEP | 2.025 | AEP
AEP Thermal TO Criteria | AEP-T29 | 246313 | DODGE TA | 246314 | DRAGOON | 1 | 34.5/34.5 | 205 | 48 |  |  | 114.62 | 54* | [6 empty] | B3_Kline 138/34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2E | Upgrade | AEP | 2.154 | AEP
AEP Thermal TO Criteria | AEP-T30 | 246300 | BEIGER | 246415 | KLINE | 1 | 34.5/34.5 | 205 | 48 |  |  | 113.98 | 56 | [6 empty] | B3_Dragoon 138/34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2F | Upgrade | AEP | 1.689 | AEP
AEP Thermal TO Criteria | AEP-T31 | 246300 | BEIGER | 246368 | VIRGIL S | 1 | 34.5/34.5 | 205 | 45 |  |  | 113.65 | 56 | [6 empty] | B3_Dragoon 138/34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2F | Upgrade | AEP | 1.689 | AEP
AEP Thermal TO Criteria | AEP-T32 | 246355 | S.BEND | 246360 | ST.MARYS | 1 | 34.5/34.5 | 205 | 27 |  |  | 103.68 | 27* | [6 empty] | B2_W Side - Goodland - Drewrey's 34.5 kV_post MOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2Y | Greenfield | AEP | 7.922 | AEP
[26 empty] | 2014_2-2Z | Upgrade | AEP | 8.588 | AEP
AEP Thermal TO Criteria | AEP-T33 | 245320 | COSHCTN8 | 245336 | N COSHCT | 1 | 34.5/34.5 | 205 | 22 |  |  | 108.13 | 22* | [6 empty] | 05NEWCOM-NEWCMTEQ |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2X | Upgrade | AEP | 5.09 | AEP
AEP Thermal TO Criteria | AEP-T34 | 245018 | SPEIDEL | 245025 | W BETHSD | 1 | 69/69 | 205 | 31 |  |  | 104.98 | 31* | [6 empty] | 7707_B2_TOR725 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2V | Upgrade | AEP | 30 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2W | Greenfield | AEP | 110 | AEP
AEP Thermal TO Criteria | AEP-T35 | 244980 | BELMONT | 245025 | W BETHSD | 1 | 69/69 | 205 | 31 |  |  | 104.27 | 31* | [6 empty] | 7707_B2_TOR725 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2V | Upgrade | AEP | 30 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2W | Greenfield | AEP | 110 | AEP
AEP Thermal TO Criteria | AEP-T36 | 245008 | DTE COAL | 245011 | ROBYVILL | 1 | 69/69 | 205 | 31 |  |  | 105.01 | 31* | [6 empty] | 7707_B2_TOR725 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2V | Upgrade | AEP | 30 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2W | Greenfield | AEP | 110 | AEP
AEP Thermal TO Criteria | AEP-T37 | 243106 | 05SOMERT | 245017 | SOMERTON | 1 | 69/138 | 205 | 70 |  |  | 110.46 | 70* | [6 empty] | 7707_B2_TOR725 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2V | Upgrade | AEP | 30 | AEP
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2W | Greenfield | AEP | 110 | AEP
AEP Thermal TO Criteria | AEP-T38 | 245939 | LOCKWOOD | 245942 | MOUNDVIL | 1 | 69/69 | 205 | 41 |  |  | 108 | 41* | [6 empty] | 53_B2_TOR587A |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T39 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 124.59 | 41* | [6 empty] | 53_B2_TOR587A |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T40 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 120.69 | 41* | [6 empty] | 1282_B3_05WBELLA 345-1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T41 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 116.01 | 41* | [6 empty] | 41_B2_TOR544 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T42 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 112.89 | 41* | [6 empty] | 4848_B1_05TIDD 138-1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T43 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 172.26 | 41* | [6 empty] | 5213_B2_TOR773 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T44 | 245922 | C.COL IR | 245938 | KAMMER | 1 | 69/69 | 205 | 41 |  |  | 106 | 41* | [6 empty] | Base Case |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2M | Upgrade | AEP | 26 | AEP
AEP Thermal TO Criteria | AEP-T45 | 245039 | FT STB 1 | 245045 | HIGH ST | 1 | 69/69 | 205 | 54 |  |  | 109.59 | 100 | [6 empty] | 5187_B2_TOR753 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Removed from Window 2
AEP Thermal TO Criteria | AEP-T46 | 245161 | PEKIN | 247252 | BANE SS | 1 | 23/23 | 205 | 10 |  |  | 198 | 33 | [6 empty] | Base Case |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T47 | 245161 | PEKIN | 245162 | PEKIN | 1 | 69/23 | 205 | 12 |  |  | 159 | Transformer | [6 empty] | Base Case |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T48 | 245043 | HAMMSVLL | 245044 | HAMMSVLL | 1 | 69/23 | 205 | 10 |  |  | 270 | Transformer | [6 empty] | Pekin-Bane-23kV |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T49 | 245033 | AUGUSTA | 0 24725 | 2 BANE SS | 1 | 23/23 | 205 | 10 |  |  | 191 | 33 | [6 empty] | Pekin-Bane-23kV |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T50 | 245060 | SUMMITVL | 245061 | SUMMTVL8 | 1 | 23/23 | 205 | 10 |  |  | 219 | 10* | [6 empty] | Pekin-Bane-23kV |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T51 | 245161 | PEKIN | 245162 | PEKIN | 1 | 69/23 | 205 | 14 |  |  | 225 | Transformer | [6 empty] | Hammondsville-Salineville-23kV |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T52 | 245161 | PEKIN | 247252 | BANE SS | 1 | 23/23 | 205 | 10 |  |  | 232 | 33 | [6 empty] | Hammondsville-Salineville-23kV |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2N | Upgrade | AEP | 9.3 | AEP
AEP Thermal TO Criteria | AEP-T53 | 243659 | BELFN5EQ | .0 2446 | 60 BELLEFNT | 1 | 69/999 | 205 | 100 |  |  | 120 | Transformer | [6 empty] | 333_B3_05BELLF1 138-2_woMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2L | Upgrade | AEP | 31.65 | AEP
AEP Thermal TO Criteria | AEP-T54 | 246179 | ALBION- | 246226 | ALBION Z | 1 | 69/69 | 205 | 50 |  |  | 110 | 50 | [6 empty] | 7913_B2_TOR12911837_WOMOAB |  | TO criteria_AEP_2018.sav |  | 2018-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2G | Upgrade | AEP | 0.2 | AEP
AEP Voltage TO Criteria | AEP-V1 | 244520 | TONEYFRK |  |  |  | 46 | 205 | [5 empty] | 0.8691 | 0.9596 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V2 | 244541 | CYCLONE |  |  |  | 46 | 205 | [5 empty] | 0.8691 | 0.9597 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V3 | 244481 | LATROBE |  |  |  | 46 | 205 | [5 empty] | 0.8725 | 0.9793 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V4 | 244537 | CRANEC2 |  |  |  | 46 | 205 | [5 empty] | 0.8749 | 0.9649 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V5 | 244536 | CRANEC1 |  |  |  | 46 | 205 | [5 empty] | 0.8749 | 0.9649 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V6 | 244505 | PARDEE |  |  |  | 46 | 205 | [5 empty] | 0.886 | 0.9594 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V7 | 244526 | THREEFRK |  |  |  | 46 | 205 | [5 empty] | 0.9005 | 0.9619 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V8 | 244813 | EMMONS |  |  |  | 46 | 205 | [5 empty] | 0.9018 | 0.9477 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V9 | 244817 | ROUNDBOT |  |  |  | 46 | 205 | [5 empty] | 0.9025 | 0.9478 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V10 | 244526 | THREEFRK |  |  |  | 46 | 205 | [5 empty] | 0.9027 | 0.9619 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V11 | 244821 | PEYTONA |  |  |  | 46 | 205 | [5 empty] | 0.9031 | 0.9466 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V12 | 244505 | PARDEE |  |  |  | 46 | 205 | [5 empty] | 0.9039 | 0.9594 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V13 | 244814 | PENN VA |  |  |  | 46 | 205 | [5 empty] | 0.9039 | 0.9517 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V14 | 244820 | MIKESRUN |  |  |  | 46 | 205 | [5 empty] | 0.904 | 0.9517 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V15 | 247099 | SHABDUE |  |  |  | 46 | 205 | [5 empty] | 0.9043 | 0.9498 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V16 | 244813 | EMMONS |  |  |  | 46 | 205 | [5 empty] | 0.9052 | 0.9477 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V17 | 244817 | ROUNDBOT |  |  |  | 46 | 205 | [5 empty] | 0.9056 | 0.9478 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V18 | 244821 | PEYTONA |  |  |  | 46 | 205 | [5 empty] | 0.9062 | 0.9466 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V19 | 244814 | PENN VA |  |  |  | 46 | 205 | [5 empty] | 0.9072 | 0.9517 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V20 | 244820 | MIKESRUN |  |  |  | 46 | 205 | [5 empty] | 0.9072 | 0.9517 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V21 | 247099 | SHABDUE |  |  |  | 46 | 205 | [5 empty] | 0.9074 | 0.9498 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V22 | 244811 | BOONE |  |  |  | 46 | 205 | [5 empty] | 0.9078 | 0.9584 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V23 | 244816 | HOPKINSF |  |  |  | 46 | 205 | [5 empty] | 0.9091 | 0.9441 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V24 | 244811 | BOONE |  |  |  | 46 | 205 | [5 empty] | 0.911 | 0.9584 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V25 | 244520 | TONEYFRK |  |  |  | 46 | 205 | [5 empty] | 0.9116 | 0.9596 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V26 | 244541 | CYCLONE |  |  |  | 46 | 205 | [5 empty] | 0.9116 | 0.9597 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V27 | 244816 | HOPKINSF |  |  |  | 46 | 205 | [5 empty] | 0.9121 | 0.9441 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V28 | 244819 | MAXINE |  |  |  | 46 | 205 | [5 empty] | 0.9122 | 0.9471 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V29 | 244819 | MAXINE |  |  |  | 46 | 205 | [5 empty] | 0.9152 | 0.9471 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V30 | 244536 | CRANEC1 |  |  |  | 46 | 205 | [5 empty] | 0.9171 | 0.9649 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V31 | 244537 | CRANEC2 |  |  |  | 46 | 205 | [5 empty] | 0.9172 | 0.9649 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V32 | 244818 | CAMPCRK |  |  |  | 46 | 205 | [5 empty] | 0.9192 | 0.9819 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V33 | 244479 | CHAP |  |  |  | 69 | 205 | [5 empty] | 0.9198 | 0.9844 |  |  |  |  | 5356_B2_TOR12638 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V34 | 244520 | TONEYFRK |  |  |  | 46 | 205 | [5 empty] | 0.8691 | 0.9596 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V35 | 244541 | CYCLONE |  |  |  | 46 | 205 | [5 empty] | 0.8691 | 0.9597 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V36 | 244481 | LATROBE |  |  |  | 46 | 205 | [5 empty] | 0.8725 | 0.9793 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V37 | 244537 | CRANEC2 |  |  |  | 46 | 205 | [5 empty] | 0.8749 | 0.9649 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V38 | 244536 | CRANEC1 |  |  |  | 46 | 205 | [5 empty] | 0.8749 | 0.9649 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V39 | 244505 | PARDEE |  |  |  | 46 | 205 | [5 empty] | 0.886 | 0.9594 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V40 | 244526 | THREEFRK |  |  |  | 46 | 205 | [5 empty] | 0.9005 | 0.9619 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V41 | 244813 | EMMONS |  |  |  | 46 | 205 | [5 empty] | 0.9018 | 0.9477 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V42 | 244817 | ROUNDBOT |  |  |  | 46 | 205 | [5 empty] | 0.9025 | 0.9478 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V43 | 244526 | THREEFRK |  |  |  | 46 | 205 | [5 empty] | 0.9027 | 0.9619 |  |  |  |  | 8758_B3_BECCO 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V44 | 244821 | PEYTONA |  |  |  | 46 | 205 | [5 empty] | 0.9031 | 0.9466 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V45 | 244505 | PARDEE |  |  |  | 46 | 205 | [5 empty] | 0.9039 | 0.9594 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V46 | 244814 | PENN VA |  |  |  | 46 | 205 | [5 empty] | 0.9039 | 0.9517 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V47 | 244820 | MIKESRUN |  |  |  | 46 | 205 | [5 empty] | 0.904 | 0.9517 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V48 | 247099 | SHABDUE |  |  |  | 46 | 205 | [5 empty] | 0.9043 | 0.9498 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V49 | 244813 | EMMONS |  |  |  | 46 | 205 | [5 empty] | 0.9052 | 0.9477 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V50 | 244817 | ROUNDBOT |  |  |  | 46 | 205 | [5 empty] | 0.9056 | 0.9478 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V51 | 244821 | PEYTONA |  |  |  | 46 | 205 | [5 empty] | 0.9062 | 0.9466 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V52 | 244814 | PENN VA |  |  |  | 46 | 205 | [5 empty] | 0.9072 | 0.9517 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V53 | 244820 | MIKESRUN |  |  |  | 46 | 205 | [5 empty] | 0.9072 | 0.9517 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V54 | 247099 | SHABDUE |  |  |  | 46 | 205 | [5 empty] | 0.9074 | 0.9498 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V55 | 244811 | BOONE |  |  |  | 46 | 205 | [5 empty] | 0.9078 | 0.9584 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V56 | 244816 | HOPKINSF |  |  |  | 46 | 205 | [5 empty] | 0.9091 | 0.9441 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V57 | 244811 | BOONE |  |  |  | 46 | 205 | [5 empty] | 0.911 | 0.9584 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V58 | 244520 | TONEYFRK |  |  |  | 46 | 205 | [5 empty] | 0.9116 | 0.9596 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V59 | 244541 | CYCLONE |  |  |  | 46 | 205 | [5 empty] | 0.9116 | 0.9597 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V60 | 244816 | HOPKINSF |  |  |  | 46 | 205 | [5 empty] | 0.9121 | 0.9441 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V61 | 244819 | MAXINE |  |  |  | 46 | 205 | [5 empty] | 0.9122 | 0.9471 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V62 | 244819 | MAXINE |  |  |  | 46 | 205 | [5 empty] | 0.9152 | 0.9471 |  |  |  |  | 6027_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V63 | 244536 | CRANEC1 |  |  |  | 46 | 205 | [5 empty] | 0.9171 | 0.9649 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V64 | 244537 | CRANEC2 |  |  |  | 46 | 205 | [5 empty] | 0.9172 | 0.9649 |  |  |  |  | 8756_B3_SKINFORK 46.0-T1 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
AEP Voltage TO Criteria | AEP-V65 | 244818 | CAMPCRK |  |  |  | 46 | 205 | [5 empty] | 0.9192 | 0.9819 |  |  |  |  | 8394_B2_TOR120_WOMOAB |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2K | Greenfield | AEP | 43.18 | AEP
AEP Voltage TO Criteria | AEP-V66 | 244479 | CHAP |  |  |  | 69 | 205 | [5 empty] | 0.9198 | 0.9844 |  |  |  |  | 5356_B2_TOR12638 |  | TO criteria_AEP_2019.sav |  | 2019-06-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-2U | Greenfield | AEP | 25.98 | AEP
EKPC Thermal TO Criteria | EKPC-T1 | 341215 | 2BULLITT CO | 342700 | 5BULLITT CO | 1 | 69/161 | 320 | 139 |  |  | 98.5 | Transformer | [6 empty] | BROWN3 & HardinCoXfr |  | TO criteria_EKPC_2018-19W.sav |  | 2019-12-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-9A | Upgrade | EKPC | 1.29 | EKPC
EKPC Thermal TO Criteria | EKPC-T2 | 341215 | 2BULLITT CO | 342700 | 5BULLITT CO | 1 | 69/161 | 320 | 139 |  |  | 118.5 | Transformer | [6 empty] | BROWN3 & HardinCoXfr |  | TO criteria_EKPC_2023-24W.sav |  | 2019-12-01 | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-9A | Upgrade | EKPC | 1.29 | EKPC
JCPL Thermal TO Criteria | JCPL-T1 | 206929 | 28ALLENHUR | 206937 | 28ELBERON | 1 | 35/35 | 228/228 | 52 | 103.65 | 105.29 | [7 empty] | Single | 'LONG_BR-BATH_AVE' |  | 2018_FYS_50-50_final_JCPL.sav |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4F | Upgrade | First Energy | 14.76 | JCPL
[26 empty] | 2014_2-4G | Upgrade | First Energy | 1.3 | JCPL
JCPL Thermal TO Criteria | JCPL-T2 | 206946 | 28LONG BR | 206947 | 28BATH AVE | 1 | 35/35 | 228/228 | 52 | 103.65 | 105.06 | [7 empty] | Single | 'ALLENHURST-ELBERON' |  | 2018_FYS_50-50_final_JCPL.sav |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-4F | Upgrade | First Energy | 14.76 | JCPL
[26 empty] | 2014_2-4G | Upgrade | First Energy | 1.3 | JCPL
Dominion Thermal TO Criteria | DOM-1 | 314068 | 6OX | 314919 | 8OX | 2 | 500/230 | 345/345 | 1021.6 |  | 104.4 | [7 empty] | Line_FB | OXH1T561 |  | Dominion 2019 RTEP Case with PPT5 & YORK3 Scaled.sav |  |  |  | 2014_2-1A | Upgrade | Dominion | 7.25 | Dominion
[25 empty] | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-1B | Upgrade | Dominion | 1.24 | Dominion
Dominion Thermal TO Criteria | DOM-2 | 314134 | 6CRANES | 314142 | 6STAFORD | 1 | 230/230 | 345/345 | 722 |  | 101.1 | [7 empty] | Single | LN 568 |  | Dominion 2019 RTEP Stress Case - No Possum 6 with YT3 and PP5 scaled.sav |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-1C | Upgrade | Dominion | 7.12 | Dominion
Dominion Thermal TO Criteria | DOM-3 | 314901 | 8BATH CO | 314912 | 8LEXNGTN | 1 | 500/500 | 345/345 | 3118 |  | 95.4 | [7 empty] | Single | LN 548 |  | Dominion 2019 RTEP Stress Case - No Possum 6 with YT3 and PP5 scaled.sav |  |  | Removed from Window 2
Dominion Thermal TO Criteria | DOM-4 | 314758 | 6GORDNVL | 314757 | 3GORDNV | 2 | 230/115 | 345/345 | 250.9 |  | 94.8 | [7 empty] | Single | LN 2135 |  | 2018_RTEP_MTX_05222013_DVPAnalysis Stress No Front Royal.sav |  |  | Pratts Area Analysis Ongoing | 2014_2-13A | Greenfield | Dominion/First Energy | 149.3 | Dominion
[25 empty] | Pratts Area Analysis Ongoing | 2014_2-13B | Greenfield | Dominion/First Energy | 201.2 | Dominion
[25 empty] | Pratts Area Analysis Ongoing | 2014_2-13C | Upgrade | Dominion/First Energy | 103.7 | Dominion
[25 empty] | Pratts Area Analysis Ongoing | 2014_2-13D | Upgrade | Dominion/First Energy | 91.47 | Dominion
Dominion Thermal TO Criteria | DOM-5 | Dominion 100 MW Radial Load Planning Criteria violation | [5 empty] | 345/345 | N/A |  | N/A | [7 empty] | Single | LN 4 |  | N/A |  |  | Preliminary Recomendation of this project at 1/7/2015 TEAC | 2014_2-1D | Upgrade | Dominion | 1.67 | Dominion
[26 empty] | 2014_2-7A | Greenfield | Northeast Transmission Development | 23 | Dominion
[26 empty] | 2014_2-10A | Greenfield | Nextera Energy Transmission | 12.71 | Dominion
[26 empty] | 2014_2-10B | Greenfield | Nextera Energy Transmission | 6.1 | Dominion