## Version History
PJM 2014 RTEP Proposal Window #2 Addendum 2 Tracking Spreadsheet
Proposal Window: | 2014 RTEP Proposal Window 2 Addendum 2
Window Opening Date: | 2015-02-24
Window Closing Date: | 2015-03-12
Current Spreadsheet Version | V1
V1: Original Posting for 4/6/2015

## Tracking by Proposal
PJM 2014 RTEP Proposal Window #2 Addendum 2 Tracking Spreadsheet
Proposal Window: | 2014 RTEP Proposal Window 2 Addendum 2
Window Opening Date: | 2015-02-24
Window Closing Date: | 2015-03-12
Current Spreadsheet Version | V1
Project ID | Upgrade/Greenfield | Proposing Entity | Cost ($M) | Target Zone | kV Level | Analysis Type | FG # | Major Components
2014_2B-1A | Greenfield | Transource | 16.13 | Meted | 230/115 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Build a new 230/115 kV Station. Install 3-230 kV breakers, 2-115 kV breakers, and a 230/115 kV transformer. Approximatly 2 miles of new double circuit 115kV transmission line.
2014_2B-1B | Greenfield | Transource | 10.55 | Meted | 115 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Allen - Williams Grove (PPL's Cumberland-West Shore 230/69kV Station S0859) 115kV project will build a new 115kV single ckt line from METED's Allen Station to Williams Grove station. Williams Grove station will incorporate a new 230/115kV transformer (300 MVA) and install a 115kV breaker as part of the proposed project. We assume that PPL will still cut in the 2-69kV lines between Cumberland and West Shore as well as build 69kV lines to West Carlisle and Carlisle Barack Stations. Allen Station will have to be expanded to incorporate the new 115kV line including 2-115kV breakers.
2014_2B-2A | Upgrade | First Energy | 0.96 | Meted | 115 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Install a 28.8 MVAR 115 kV capacitor at the Mountain substation. Capacitor should be switched on prior to the second contingency.
2014_2B-3A | Greenfield | Northeast Transmission Development | 11.1 | Meted | 115/69 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Approximately 2.5-mile double-circuit 115 kV transmission line interconnecting the existing Allen-Roundtop 115 kV transmission line to a new 115/69 kV substation ("Dogwood Run") adjacent to the PPL S0859 230/69 kV substation
2014_2B-3B | Greenfield | Northeast Transmission Development | 13.9 | Meted/PPL | 115/69 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Approximately 2.5-mile double-circuit 115 kV transmission line interconnecting the existing Allen-Roundtop 115 kV transmission line to a new 115/69 kV substation ("Dogwood Run") adjacent to the PPL S0859 230/69 kV substation with 60 MVAR Fast Switched Shunt.
2014_2B-3C | Greenfield | Northeast Transmission Development | 13.3 | Meted | 115/230 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Approximately 2.5-mile double-circuit 115 kV transmission line interconnecting the existing Allen-Roundtop 115 kV transmission line to a new 115/230 kV substation ("Dogwood Run") adjacent to the PPL S0859 230/69 kV substation
2014_2B-3D | Greenfield | Northeast Transmission Development | 17.4 | Meted/PPL | 115/230 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Approximately 2.5-mile double-circuit 115 kV transmission line interconnecting the existing Allen-Roundtop 115 kV transmission line to a new 115/230 kV substation ("Dogwood Run") adjacent to the PPL S0859 230/69 kV substation with 90 MVAR Fast Switched Shunt.
2014_2B-3E | Greenfield | Northeast Transmission Development | 16.9 | Meted | 115/500 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Build 500/115 kV Substation (Dogwood Run) Interconnecting Juniata-Three Mile Island 500 kV Line to Allen-Roundtop 115 kV Line
2014_2B-3F | Greenfield | Northeast Transmission Development | 25.5 | Meted/PPL | 115/500 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Build 500/115 kV Substation (Dogwood Run) Interconnecting Juniata-Three Mile Island 500 kV Line to Allen-Roundtop 115 kV Line with 2.5-mile 115 kV Line to a new 115/69 kV substation adjacent to the PPL S0859 230/69 kV substation.
2014_2B-4A | Greenfield | PPL/FE | 11.94 | Meted/PPL | 230/115 | N-1-1 Voltage Drop | N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14 | Expand the existing Allen substation, and connect via new ~2.6 Mile 115kV transmission to PPL's Williams Grove Substation, with transformation to 230kV at Williams Grove Substation