## Setup
Enter Stakeholder Committee Name in cell A2:
Distributed Resources Subcommittee (DISRS)
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Hybrid Resources Enhancements (Hybrid Phase 3)

## 1. Interest Identification
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure that all types of hybrid resources that seek to participate in PJM’s markets have a clearly-defined set of applicable rules and requirements in PJM’s governing documents.
2 | Ensure that definitions properly capture hybrid resources’ operational characteristics. <and allow hybrid resources to participate in pjm wholesale markets on a level play field. (equality of oppurtunity)>
3 | Ensure alignment between Tariff and Manual language regarding all aspects of the hybrid resources participation model.
4 | <Clarity around fuel cost policy for hybrids>
5 | <state how rules work for connections with loads and connections without loads>
6 | Allow hybrid resources to participate in PJM wholesale markets on a level playing field.
7 | Define a fuel cost rules for hybrid resources.
8 | Clarify how market participation rules account for connections with and without loads.
9
10
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
* | Implementation
Markets Items
1 | Definitions |  | “Hybrid Resource” shall mean an Energy Resource or a Generation Capacity Resource composed of more than one component behind the same Point of Interconnection operating in the capacity, energy, and/or ancillary services market(s) as a single integrated resource, whereby each component is a separate generation and/or storage technology type. A Hybrid Resource forms all or part of a Mixed Technology Facility. “Open-Loop Hybrid Resource” shall mean a Hybrid Resource with a storage component that is physically and contractually capable of charging its storage component from the grid. “Closed-Loop Hybrid Resource” shall mean a Hybrid Resource without a storage component, or that is physically or contractually incapable of charging from the grid. | Status quo definition for "Hybrid Resource". Market participant determines and indicates to PJM whether or not the unit will operate in the market as an open or closed-loop resource depending on whether or not it charges the storage component from the grid.
2 | Modeling Energy/Ancillary Services |  | A Hybrid Resource consisting solely of inverter-based components with at least one storage component is eligible to participate in Energy and Ancillary Services markets using a similar approach as the Energy Storage Resource participation model. A Hybrid Resource consisting solely of non-storage inverter-based components is eligible to participate in Energy and Ancillary Services markets using a similar energy market participation model as used by solar/wind resources.
3 | Regulation |  | Hybrid Resources can participate in Regulation if they meet performance requirements. Unlike Energy Storage Resources, Hybrids with a battery component cannot provide regulation-only. | Status quo
4 | Reserves |  | Hybrid Resources are eligible to provide reserves, with the exception of non-synchronized reserves and offline secondary reserves. Hybrids are not considered available by default, and must submit specific reserve offers to be considered. The reserves quantity is determined by the Market Seller, not by PJM. Unlike Energy Storage Resources, Hybrid Resources with a battery component cannot provide reserves-only. | Status quo AND Hybrid resources comprised exclusively of inverter-based generation components are not eligible to provide reserves (and do not have a reserves must offer) unless an exception is requested and approved. |  |  |  |  | Low
5 | Capacity Market Must Offer |  | A Hybrid Resource Resources consisting exclusively of components that in isolation would be exempt from the RPM must offer requirement is itself exempt. | A Hybrid Resource with any component that is not exempt from the RPM must offer requirement is itself not exempt. |  |  |  |  | Low - Medium
6 | Energy Market Must Offer - ESR |  | Hybrid Resources and Energy Storage Resources with a capacity commitment may meet their must offer requirements by self-scheduling (i.e., self-commit) into the energy market or may allow the Day-ahead Market to schedule by offering the unit as a dispatchable resource. Energy Storage Resources and Hybrid Resources consisting of only Intermittent and/or Storage components, may offer quantities that vary from their cleared capacity quantity. | Status quo AND The ESR must offer/self-schedule at least its total energy quantity, based on the ICAP and duration, during a 24 hr period. E.g., a 10 MW, 4-hour battery must offer at least 40 MWh of energy in the DA market to meet the must offer requirement. | Status quo AND The ESR must offer/self-schedule at their ICAP for the number of hours equal to its duration. E.g., a 10 MW, 4-hr battery must offer 10 MW in at least four hours to meet the must offer requirement. | Status quo AND The ESR must offer/self-schedule at their ICAP for the number of hours equal to its duration. E.g., a 10 MW, 4-hr battery must offer 10 MW in at least four hours to meet the must offer requirement. The hours must reflect peak system need.
6a | Energy Market Must Offer - Hybrid Resources |  | Same as ESR
7 | Charging Energy |  | ESR and Open-Loop Hybrid Resoures are permitted to buy Direct Charging Energy in the energy market. Charging energy for ESR and Open-Loop Hybrid Resources takes transmission service under certain circumstances (consistent with Order 841), and therefore pays additional non-LMP charges under certain conditions. [See Manual 27 Section 8 and Manual 28 Section 22.] | [5 empty] | Low - High
8 | Charging Energy vs. Station Power |  | Direct Charging Energy is not Station Power.
9 | Uplift Eligibility & Calculation: Make-Whole Payment |  | Hybrid Resources are eligible for uplift. BOR Credit if pool-scheduled and revenues < offer. (Tariff Att K, Appdx, Section 3.2.3 (e))
10 | Uplift Eligibility & Calculation: LOC |  | The LOC-eligible quantity is based on the lesser of the PJM's backcast of the projected output, inclusive of state of charge, or the desired MW amount for the resource determined according to the point on the final offer curve corresponding real-time LMP for the settlement interval at the resource’s bus, adjusted for any reduction in MW due to regulation, synch reserve, or secondary reserve assignments. (Tariff Att K, Appdx, Section 3.2.3 (f-4)) [Approved as part of phase II; not yet implemented.]
11 | Resource Classification Requirements |  | A Mixed Technology Facility with significant interactions between the generation and/or storage components (i.e., these cannot operate independently) is required to participate in PJM’s Markets as a single Hybrid Resource. A Mixed Technology Facility with components that can operate independently may select to participate as either a Hybrid Resource or as multiple Co-Located Resources. Hybrid Resources are classified as either open-loop or close-loop based on whether or not they are able to physically and contractually charge from the grid. (See definions.) | [5 empty] | Medium - High
12 | Resource Classification Process |  | Capacity resources: classification can be changed every 5 years to match the frequency with which a technology may change its ELCC resource classification. The same classification must be chosen in both the capacity and energy markets for an applicable delivery year. Energy market only: classification can be changed 1x per calendar year with notice to PJM by May 30 for the upcoming Jan 1 to Dec 31 participation months. | New resources must inform PJM of their desired classification least 6 (six) months ahead of their planned in-service date by contacting Member Relations at custsvc@pjm.com. Capacity resources: A market participant that plans to provide capacity must inform PJM of their intent to participant as a hybrid resource by December 1 (ahead of the 3rd IA) for the upcoming delivery year by emailing the RPM hotline at rpm_hotline@pjm.com. All changes in classification made by an existing capacity resource must be communicated to PJM in the same manner. All other status quo requirements continue to apply. Energy market only: All existing energy-only resources may change their classification (e.g., open to closed-loop, hybrid to co-located, etc.) by contacting Member Relations at custsvc@pjm.com. All other status quo requirements continue to apply.
13 | NITSA Requirements |  | Pro forma NITSA in Tariff Attachment F-2 covers Open-Loop Hybrid Resources.
Operations Items
14 | Metering & Telemetry |  | Hybrid Resources must have telemetry at the POI for MW and MVAR, and must have revenue metering at the POI for MWh, consistent with any other generation resource. Each component is required to provide telemetry. Telemetered submeter values for one component may be inferred as the difference between the POI telemetry and the other component telemetry (corrected for losses to the POI).
15 | State of Charge |  | Hybrids with a storage component are responsible for managing their own State of Charge. Entering SOC information in Markets Gateway is currently optional and is used for PJM research purposes only.
16 | Data Requirements for Forecasting |  | Hybrids with a wind or solar component have same data requirements as standalone wind or solar.
17 | Operating Requirements |  | An intermittent or hybrid resource’s Economic Minimum should not exceed the level of its CIR. An intermittent or hybrid resource’s Emergency Minimum should be set to 0. The output of a hybrid resource should achieve its dispatch point within 5 minutes or consistent with the resource's ramp rate bid. PJM should be notified if the response time is expected to exceed 5 minutes. The operator of a hybrid resource with a battery component that is dispatchable must indicate to PJM the hours for which the plant is operating in “intermittent-only” mode, during which time the battery is not providing power for the purpose of maintaining hybrid output consistent with PJM dispatch. Dispatchable hybrids must follow dispatch in both "intermittent-only" mode and all other hybrid modes.
18 | Outage Reporting |  | Separate reporting in eDART for each component of a hybrid resource when unavailable or derated. GADS reporting for the storage component of a hybrid resource. No eDART or GADS ticket is required for lack of solar irradiance, charging, or lack of charge.
19 | Reactive Capability: Testing |  | For a Hybrid Resource consisting entirely of inverter-based components, a single D-curve is tested. Such facilities are tested consistent with the provisions for inverter based Hybrid Resources specified in Manual 14D.
20 | Reactive Capability: D-curves |  | DC-coupled: same as ESR model (the reactive capability should be based on Inverter MVA Capability Curve) AC-coupled: For a Hybrid Resource, the composite reactive capability curve must represent the most conservative capability of the combined Generating Facility at each net MW injection point.
Cost Development Subcommittee Items - *Will not be part of final package*
21 | Cost Offers |  | The default cost offer for hybrid resources in $0.
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Distributed Resources Subcommittee (DISRS)
Hybrid Resources Enhancements (Hybrid Phase 3)
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1 | 2024-01-08 | First Draft
2
3