## Setup
Enter Stakeholder Group Name in cell A2:
[GroupName]
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
[IssueTitle]

## 1. Interest Identification
PFRSTF
Primary Frequency Response Sr. Task Force
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure adequate Primary Frequency Response during system restoration events.
2 | Ensure no degradation to BAL-003-1 performance considering the changing resource mix.
3 | Enable greater predictability and consistency of system Primary Frequency Response.
4 | Increase confidence level in generator frequency response settings including a better understanding of current generation operating modes and their impact on frequency response.
5 | Minimize generator financial impacts (i.e. headroom requirments).
6 | Implement a solution consistent with regulatory compliance and guidance (FERC/NERC)
7 | Solution should be resource-type neutral where possible.
8 | Ensure market rules won't discourage resources from providing Primary Frequency Response (i.e. 5 min settlement deviation, regulation scoring, capacity performance, performance assessment hour)
9 | Development of an apples to apples comparison to facilitate a standardized product definition. Quantify what PFR is worth.
10 | Develop a solution for the transition and coordination from primary to secondary response.
11 | Primary frequency response is bi-directional product. Capability is expected in both directions.
12 | Proactively plan for potential future requirements.
13 | Modifying the synchronized reserve to include a frequency component.
14 | Ensuring enough primary frequency response is available at all times to recover from larger system disturbances.
15 | Ensuring costs are adequately covered and compensation is covered.
16 | Visibility of frequency response to real time operators.
17 | Ensure energy storage resources are not unfairly impacted by PJM's requirements.
18 | Include an exemption process and criteria for technical or operational considerations.
19 | Tie any requirements for PFR directly to compensation
20 | Carefully consider the implications of creating a frequency response performance evaluation

## 2. Options Matrix- Design Comp.
PFRSTF
Primary Frequency Response Sr. Task Force
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F | G | H
1 | Interconnection PFR Requirement | High | Balancing Authority Requirement BAL-003-1 FRO = 258.63 MW/.1 Hz for 2017
| Individual Unit Requirement | High | New units PFR requirement is in Interconnection Service Agreement | Supplemental additional freq response for more significant events | Individual unit capability requirement for PFR | Individual unit capability requirement for PFR by resource class | Include appropriate requiremetns for energy storage resources regarding sustained response | Determine individual unit MW obligation for every resource type (no exceptions)
1a | Droop Setting | High | Not to exceed 5% (M-14D) | A: Different droop setting by resource class
1b | Deadband | High | Not to exceed +/- 36 mHz (M-14D) | A: Move to +/- 17 mHz; B: Maintain consistency with Eastern Interconnection
1c | Plant level Digital Control Systems (i.e. outerloop controls) | Low - High | Undefined | Utilize locally sensed frequency as input in control system | Digital control systems must allow unit to provide PFR | Digital control systems should if posible allow unit to provide PFR | For Blackstart or critical load units utilize locally sensed frequency as input | Control of generator output should incorporate a bias for frequency error to allow governor action. Other runbacks and overides may be used as needed to protect the generating equipment.
1d | Governor Equivalent Mode of Operation (i.e. MW setpoint) | Low - High | Unrestricted governor control (M14-D, Sec 7.1.1) | Utilize locally sensed frequency as input in control system | Governor equivalent mode of operation must allow unit to provide PFR | Governor equivalent mode of operation should if possible allow unit to provide PFR | For Blackstart or critical load units utilize locally sensed frequency as input | Include appropriate requirements for energy storage devices | The phrase from Man. 14-D "equivalent electronic speed control device" should be changed to "electronic load/frequency controller" to account for inverter based generation
1e | "Headroom/Footroom" requirement | Low | None
1f | Bi-directional Frequency Response | Low | Undefined | A: Additional manual language clarifying bi-directional requirement
1g | Automatic detection and response to local frequency measures | Low - High | M-14D | A: Additional clarifying manual language; B: Local frequency or speed measurements and autonomous control are necessary
2 | Required Resources | High | Nameplate > 75 MVA (aggregated) | Clarification of definition of aggregated resource | Apply to all smal and large, new and existing resources | Optional for all resources | Apply to all new generator interconnection (> 20 MVA; consistent with voltage schedule) and existing units > 75 MVA or consistent with FERC NOPR | Aggregation behind the POI for all generating resources | Determine individual unit MW obligation for every resource type (no exceptions)
2a | New/Existing resources | High | All resources (new and existing) with exception process (M-14D) | A: Optional for all resources; B: Required for new resources only; C: Required for all resources; D: Required for all new and existing resources (Existing units > 75 MVA)
2b | Exempt Resources | High | Nuclear generation | Resources with low capacity factors | Units greater than 25 years old | Documented exception process similar to PLS | Acquiring replacement obligation if not providing service | Need exemption process and criteria for technical or operational considerations. | None
3 | Inertial response | Low - Medium | No requirements for any resources | A: Differentiate between intertial response from govenor frequency control
4 | Performance requirement/verification | High | "System" response measured for compliance with BAL-003-1. No individual unit performance requirements. MOD-27 requirements | A: Measured individual unit performance during selected frequency events; B: Penalties for non-performance; C: Reserve right to report non-performance to FERC; D: Frequency excursions outside the 36 mHz deadband limits are rare iin the EI. Frequency excursions above 60.060 or below 59.940 would be necessary to fairly evaluate performance
5 | Compensation mechanism | High | None (included in offer) | Payment based on MW response times LMP multiplier | Opportunity cost payment if headroom is maintained to provide frequency response | Recovery through capacity market through CONE | Cost of Service structure (filed with FERC similar to Sched 2) | Market based product, similar to Regulation | Capital investment is already included in CONE. VOM is included in the CP offer. | Explore compensation for synchronous intertial capability | Develop secondary market to allow resources that can't or choose not to meet obligation to purchase PFR from othe resources. | Low
6 | Telemetry requirements | High | Manual M-01 requirements (10 seconds) | A: 2 sec. scan rate for performance assessment; B: 2 sec. scan rate on new generators; C: Generator output measurement and transmission resolution should be at least 0.1 MW or 1% (whichever is less)
7 | Additional requirements for Blackstart or Critical Load units | High | Blackstart must be capable of isochronous control (maintain voltage and frequency under varying loads (m-36) Yearly Blackstart unit testing | A: Clarify "under varying load" terminology in M-36 for Blackstart units; B: Clarify mode of operation for governor equivalent; C: For Blackstart or critical load units utilize locally sensed frequency as input | Low - Medium
8 | Treatment of regulating units | Medium | Not defined | A: Expected to provide PFR; B: Not expected to provide PFR; C: Expected to provide PFR, no impact to regulation score; D: Not expected to provide PFR during hours unit is assigned regulation
9 | Treatment of pseudo tied or dynamically scheduled units | Medium | Not defined | Pseudo-tied expected to provide PFR | Pseudo-tied not expected to provide PFR | Dynamically scheduled units expected to provide PFR | Dynamically scheduled units not expected to provide PFR | Dynamically scheduled units follow rules of native BA
10 | Treatment of units providing synchronized reserve | Medium | Not defined | A: Expected to provide PFR; B: Not expected to provide PFR; C: Expected to provide PFR, no impact to sync reserve score
11 | Treatment of CP units in Performance Assessment Hour | Medium | Not defined | A: Providing PFR should not result in PAH penalty; B: Pro-ration of frequency response service should be reflected in PAH calculation (penalty/bonus); C: Frequency response not included in PAI calculation. | Low - High
12 | Treatment of DER resources | Medium | Not defined | A: Wholesale DER would meet all frequency requirements; B: Interconnection agreement vs. WMPA | Medium
13 | Treatment of intertial synchronous motors load providing frequency response | Medium | Not defined
14 | Allowing load based frequency response service/product | Low | Not defined | A: Limit the LR capacity to % of the minimum generating reserve
15 | Implemenation Plan | High | [9 empty] | Medium - High
16 | Evaluate benefits of different resource types. Benefits factor | High | Not defined | [8 empty] | High
17 | Treatment of imbalance and operating reserve charges for units following basepoints for energy
PJM Additions
ESA Additions
AEP Additions
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
PFRSTF
Primary Frequency Response Sr. Task Force
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component |  | Detailed Description
34 | Treatment of imbalance and operating reserve charges for units following basepoints for energy | Pool scheduled and dispatchable self-scheduled resources operating above economic minimum will then be considered to be following dispatch if: 1. its actual output is between its Ramp Limited Desired MW and UDS Basepoint; 2. % off dispatch is less than or equal to 10 or 3. hourly integrated RT MWh are within five percent or 5 MW (whichever is greater) of the hourly integrated Ramp-Limited Desired MW
2 |  | <enter detailed description of this component>
3 |  | <enter detailed description of this component>
4 |  | <enter detailed description of this component>
5 |  | <enter detailed description of this component>

## 2b. Option Details
PFRSTF
Primary Frequency Response Sr. Task Force
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
2B Documented Exception Process | Nuclear. Targeted exception process for existing resources which might be different from new resources. Not allowing exceptions for units needed in restoration process. Units scheduled to retire that may require capital investment.
4 Resource Performance Measurement | Units providing regulation will not have their regulation performance score impacted. High level correct direction response. Factor in physical limitations of a unit. Telemetry failure. BAL/TRE requirement.
5 Compensation Mechanism
11 PAH hour determination
12 Treatment of DER | If interconnection service agreement is signed then PFR is required. If participating in PJM markets, then must provide PFR.

## 3. Package Matrix
PFRSTF
Primary Frequency Response Sr. Task Force
PACKAGE/ PROPOSAL MATRIX
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.
Packages
# | Design Components | Priority | Status Quo | PJM (Package A) | IMM (Package B) | AEP (Package C) | PJM Option B (Package D) | Calpine (Package E)
1 | Frequency Response Requirement | High | Balancing Authority Requirement BAL-003-1 FRO = 258.63 MW/.1 Hz for 2017 | Individual unit capability requirement for PFR | Same as PJM (option A) | Status Quo; or as mandated by NERC | Individual unit capability requirement for PFR | Individual requirement to provide through unit or purchase of service. Must have capability to provide an "up" response in order to provide Dynamic Reserves during system restoration. Must have capability to provide a "downward" response.
1a | Droop Setting | High | Not to exceed 5% (M-14D) | Status Quo | Same as PJM (option A) | Status Quo | Status Quo | Status Quo
1b | Deadband | High | Not to exceed +/- 36 mHz (M-14D) | Status Quo but maintain consistency with Eastern Interconnection | Same as PJM (option A) | Same as PJM (option A) | Status Quo but maintain consistency with Eastern Interconnection | Same as PJM (option A)
1c | Plant level Digital Control Systems (i.e. outerloop controls) | Low - High | Undefined | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop sttings. | Same as PJM (option A) | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop settings capability. | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop sttings. | Utilize locally sensed frequency as input in control system to correct unit output demand for frequency error. This should reflect the governor deadband and droop settings capability.
1d | Governor Equivalent Mode of Operation (i.e. MW setpoint) | Low - High | Unrestricted governor control (M14-D, Sec 7.1.1) | Utilize locally sensed frequency as input in control system; Governor equivalent mode of operation must allow unit to provide PFR | Same as PJM (option A) | Same as PJM (option A) | Utilize locally sensed frequency as input in control system; Governor equivalent mode of operation must allow unit to provide PFR | Same as PJM (option A)
1e | "Headroom/Footroom" requirement | Low | None | Status Quo | Same as PJM (option A) | Status Quo for normal ops; but expected (i.e. status quo) during actual system restoration | Status Quo | Status Quo for normal ops; but headroom expected to be able to be created by PJM sys ops during actual system restoration.
1f | Bi-directional Frequency Response | Low | Undefined | Additional manual language (M14D) clarifying bi-directional requirement | Same as PJM (option A) | Same as PJM (option A) | Additional manual language (M14D) clarifying bi-directional requirement | Requirement to provide through unit or purchase of both directions of Frequency Response
1g | Automatic detection and response to local frequency measures | Low - High | M-14D | Additional clarifying manual language (M14D) | Same as PJM (option A) | Same as PJM (option A) | Additional clarifying manual language (M14D) | Same as PJM (option A)
1 h | Additional FPR requirement for Substitute unit/device | [6 empty] | Additional capability as determined in accordance with maintaining 258.63 MW/.1 Hz … used for each substitute FPR commitment taken
AA-1 | Dynamic Reserve Capability Requirement |  | Dynamic Reserves are only calculated and used during system restoration. Determined by “load pick-up” factors which is the Maximum load an online generator can pick up, as a percentage of the generator’s rating (capacity), without incurring a frequency decline below safe operating levels |  |  | Not applicable; status quo |  | 5% of load pickup. Existing units exempted from requirement.
AA-2 | Additional Dynamic Reserve Capability requirement for Substitute unit/device |  | N/A |  |  | Not applicable |  | Additional load pickup capability to account for substitute unit's MWs being displaced
2 | Required Resources | High | Nameplate > 75 MVA (aggregated) | Apply to all small and large, new and existing resources. | Same as PJM (option A) | Requirement for all new resources that have entered into the PJM que on or after October 1, 2018 to obtain a Small or Large Generation Interconnection Agreement as well as existing resources seeking a MW uprate modification to their SGIA or LGIA. | New resources must follow the FERC Order 842 requirements. Existing units > 20 MW must meet the requirements in cell 2a. | Requirement for all new resources that have entered into the PJM que after October 1, 2018 to obtain a WMPA or Small or Large Generation Interconnection Agreement as well as existing resources seeking a MW uprate modification to their SGIA or LGIA. | Low
2a | New/Existing resources | High | All resources (new and existing) with exception process (M-14D) | Required for all resources | Same as PJM (option A) | Obligation to provide PFR for all new resources that have entered the PJM que to obtain a Small or Large Generation Interconnection Agreement on or after October 1, 2018. Existing resources receive an obligation to provide PFR if that have enter the PJM que to increase the MW capability in their Generation Interconnection Agreement after October 1, 2018. Performance requirements for batteries/temporary storage need developed. Combined Heat & Power that is not an exporter must have necessary equipment to provide but have no performance requirement. CHP that is an exporter have operational requirements to provide. (Summary - required of all new resources after 10/1/18; existing only if uprate MW change to interconnection agreement after 10/1/18) | All Units identified in an approved System Restoration Plan must provide an annual confirmation that they have the ability to implement processes to ensure units are capable of sustained primary frequency response (i.e. responsive to local frequency input) during system restoration situations. The confirmation would include an acknowledgement that plant operators would, within 30 minutes, be able to disable any non-protective, centralized or local equipment control functions, that impact sustained frequency response. | Obligation to provide PFR (including dynamic reserve capability) for all new resources that have entered the PJM que to obtain a WMPA, or Small or Large Generation Interconnection Agreement after October 1, 2018. Existing resources receive an obligation to provide PFR if they have enter the PJM que to increase the MW capability in their Generation Interconnection Agreement after October 1, 2018. Performance requirements for batteries/temporary storage need developed. Combined Heat & Power that is not an exporter must have necessary equipment to provide but have no performance requirement. CHP that is an exporter have operational requirements to provide. (Summary - required of all new resources after 10/1/18; existing only if uprate MW change to interconnection agreement after 10/1/18). Existing Resources: Any existing resource with current capability based on current resoource configuration/setup must continue to provide PFR capability through maintaining proper droop and deadband settings. | Low - Medium
2a1 | eDart Reporting | [6 empty] | eDart: All resources obligated to provide PFR capability must use eDart to indicate when governor control/PFR ability is out. Outage of said equipment/capability should only be done for legitamate outage purposes.
2a2 | Definition of existing resources |  |  | Existing resources are defined as resources that are in commercial operation or have a signed ISA or Pseudo-Tie Agreement, at time of FERC approval of PFR requirements. | Same as PJM (option A) | Existing resources are defined as resources that are in commercial operation or have a signed ISA or Pseudo-Tie Agreement, at time of FERC approval of PFR requirements. | Existing resources are defined as resources that are in commercial operation or have a signed ISA or Pseudo-Tie Agreement, at time of FERC approval of PFR requirements.
2b | Exempt Resources | High | Nuclear generation | Nuclear units exempt; documented exception process including deadline extensions or settings exemptions. Existing resources <=20 MW aggregated exempt. | <10 MW | Nuclear units exempt; documented exception (see "Exemption from PFR Requirement AEP Package" document) process including deadline extensions or settings exemptions. All existing resources should continue to provide levels of PFR, consistent with their current capabilities. | Nuclear units exempt; documented exception process including deadline extensions or settings exemptions. Existing resources <=20 MW aggregated exempt. All existing resources shall continue to provide levels of PFR consistent with their current capabilities. Resources identified in System Restoration Plan must meet the requirements in cell 2a. | Depending on FERC Rehearing Order; either exempt (1) Existing Nuclear as ordered by FERC and existing units technically incapable of providing under current unit configuration/setup or (2) all existing units in-service or that have entered queue before October 1, 2018. Note that Units with a requirement (such as all new units) would have option to purchase service from another resource and would not be required to provide service themselves from said unit. | Low - High
2-AA | Exempt Resources from Dynamic Reserve capability requirement | [6 empty] | Exempt existing units in-service or that have entered queue before October 1, 2018. Note that Units with a requirement (such as all new units) would have option to purchase service from another resource and would not be required to provide service themselves from said unit.
2c | Purchased Service in lieu of own unit providing |  | Not an option | Status Quo |  |  | Status Quo | This applies to resources used as a substitute. Required.
3 | Inertial response | Low - Medium | No requirements for any resources | Status Quo | Same as PJM (option A) | PJM and Transmission Owners are encouraged to study the value of synchronous inertial response in restoration, including the substitution rate of assets providing synchronous inertia to that of resources that cannot provide synchronous inertia. The following study describes the impact of low inertial response. https://arxiv.org/pdf/1312.6435.pdf | Status Quo | PJM and Transmission Owners are encouraged to study the value of synchronous inertial response in restoration, including the substitution rate of assets providing synchronous inertia to that of resources that cannot provide synchronous inertia. The following study describes the impact of low inertial response. https://arxiv.org/pdf/1312.6435.pdf | Medium
4 | Performance requirement/verification | High | "System" response measured for compliance with BAL-003-1. No individual unit performance requirements. MOD-27 requirements | Measured individual unit performance during selected frequency events. Units operating above 95% Eco Max or below Eco Min+(5% x Eco Max) should be exempted from performance assessment. Unit will need to provide 50% of expected reponse to Pass (in MW). Pass/Fail assessment will be down on a quarterly basis and looks at a 12 month rolling window and a minimum number of 3 events will be used for evaluation. Events will be selected when frequency is outside +/- 40mHz, a frequency min/max of +/- 53mHz is observed, and frequency stays outside of dead band for 60 consecutive seconds. PJM will provide performance scores to resource owners during the 24 month implementation period, however "official" scoring will not take place until following the 24 month implementation period. | Same as PJM (option A) | Measure individual unit performance (solar and windfarms at point of interconnection) during selected frequency events for new resources, or for existing resources that become newly obligated to provide PFR. Units operating above 95% Eco Max or below Eco Min+(5% x Eco Max) will be exempted from performance assessment. Unit with eDART ticket representing outage of equipment necessary for frequency response exempted from performance assessment. Expected performance will evolve to take into account operational characteristics of asset type. Units will need to provide 50% of expected response to Pass (in MW). Pass/Fail assessment will be performed on a quarterly basis and look at a 12 month rolling window. PJM will use the average of at least 6 events to judge compliance. Frequency response performance evaluations can be made when the system frequency deviation is greater than +/- 53mHz and frequency deviation remains greater than a 36 mHZ of dead band for 60 consecutive seconds. All resources shall be able to review an assessment of their performance. The performance score is utilized to help the resource evaluate potential changes and for PJM to consider any future modifications to scoring based on technology type. | Measured individual unit performance during selected frequency events. Units operating above 95% Eco Max or below Eco Min+(5% x Eco Max) should be exempted from performance assessment. Unit will need to provide 50% of expected reponse to Pass (in MW). Pass/Fail assessment will be down on a quarterly basis and looks at a 12 month rolling window and a minimum number of 3 events will be used for evaluation. Events will be selected when frequency is outside +/- 40mHz, a frequency min/max of +/- 53mHz is observed, and frequency stays outside of dead band for 60 consecutive seconds. PJM will provide performance scores to resource owners during the 24 month implementation period, however "official" scoring will not take place until following the 24 month implementation period. | PJM shall establish a measure of "Poor Performance". Measure individual unit performance (solar and windfarms at point of interconnection) during selected frequency events for new resources, or for existing resources that become newly obligated to provide PFR. Units operating above 95% Eco Max or below Eco Min+(5% x Eco Max) will be exempted from performance assessment. Unit with eDART ticket representing outage of equipment necessary for frequency response exempted from performance assessment. Units will need to provide 50% of expected response to Pass (in MW). Pass/Fail assessment may be performed after a significant frequency event on the system as part of significant event analysis. PJM will use quantitative analysiis taking into account circumstances at indivvidual units to judge Pass/Fail outcomes. Frequency response performance evaluations can be made when the system frequency deviation is significant and frequency deviation remains greater than a 36 mHZ of dead band for 120 consecutive seconds. All resources shall be able to review an assessment of their performance before finalizing. The performance score is utilized to help the resource evaluate potential changes. Must be for entire facility and whole heat train, b/c steam turbine not a prime mover. | Medium - High
| Resource Reporting to PJM |  |  |  |  | see design component #7 |  | Each year a new resource or obligated existing resource must certify to PJM that it has and will continue to provide PFR and Dynamic Reserves either through its own resource or through arrangement with a third party. All third parties must be identified. Third parties providing PFR and/or Dynamic reserves are also required to certify that their resources are and will continue to provide PFR and Dynamic Reeserves.
4a | Resource Performance Reporting to FERC |  | PJM retains right to report any OATT violation to FERC | STATUS QUO - No specific triggers for reporting violations to FERC. Monitor for chronic non-performance |  |  | STATUS QUO - No specific triggers for reporting violations to FERC. Monitor for chronic non-performance | Each year a new resource or obligated existing resource that fails to certify to PJM that it has and will continue to provide PFR and Dynamic Reserves may be reported to FERC. Additionally, a new resource or newly obligated existing resource that performs poorly (Poor Performance during a system event anlyzed by PJM could have its nonperformance reported to FERC after January 1, 2021 if PJM deems the resource to have not fixed the causal issues or if PJM deems the resource to potentially have chronic PFR performance issues. Should be allowed to remedy performance issues in a timely fashion.
5 | Compensation mechanism | High | None (included in offer) | Cost recovery structure submitted to PJM and IMM for one-time recovery of capital costs associated with PFR (similar process to paragraph 17 of schedule 6a) for existing resources (resources that are in commercial operation or have a signed ISA or Pseudo-Tie Agreement at time of FERC approval of PFR requirements). 1 year cost recovery, no incentive, no rate of return - Capital recovery (equipment or control systems) -----One time recovery submitted to PJM and IMM - Ongoing maintenance --> Include in VOM or file for FERC rate inaccordance with existing rules in M-15 - Heat rate loss --> Update heat rate curve and include in energy offer | The Capacity Market already provides opportunity for compensation for frequency response related equipment costs and going forward avoidable costs for new and existing resources. The Energy Market already provides/allows recovery of incremental output related costs associated with providing frequency response. | Resources could file a cost of service methodology for compensation and approval at FERC. Ongoing maintenance in M-15. | Cost recovery structure submitted to PJM and IMM for one-time recovery of capital costs associated with PFR (similar process to paragraph 17 of schedule 6a) for existing resources (resources that are in commercial operation or have a signed ISA at time of FERC approval of PFR requirements). 1 year cost recovery, no incentive, no rate of return - Capital recovery (equipment or control systems) -----One time recovery submitted to PJM and IMM - Ongoing maintenance --> Include in VOM or file for FERC rate inaccordance with existing rules in M-15 - Heat rate loss --> Update heat rate curve and include in energy offer | For Unit Meeting Its Own Requirements: Cost recovery structure submitted to PJM and IMM for one-time recovery of capital costs associated with PFR (similar process to paragraph 17 of schedule 6a) for existing resources (resources that are in commercial operation or have a signed ISA or Pseudo-Tie Agreement at time of FERC approval of PFR requirements). 1 year cost recovery, no incentive, 10% rate of return - Capital recovery (equipment or control systems) -----One time recovery submitted to PJM and IMM - Ongoing maintenance --> Include in VOM or file for FERC rate. Update rules accordingly in M-15 - Heat rate loss --> Update heat rate curve and include in energy offer | High
5a | Compensation Mechanism for Substituted Unit (the original unit with obligation) |  |  | See Row 5 |  |  | See Row 5 | Can include cost of purchasing service from substitute unit in cost-based offers. Based on cost spread out over some expected number of run hours. Update rules in Manual 15
5b | Compensation Mechanism of Substitute Unit/Device |  | Not Applicable | N/A |  |  | N/A | Payment from unit being substituted.
6 | Telemetry requirements | High | Manual M-01 requirements (10 seconds) | Status Quo | Same as PJM (option A) | Same as PJM (option A) | Status Quo | Same as PJM (option A)
7 | Additional requirements for Blackstart or Critical Load units | High | Blackstart must be capable of isochronous control (maintain voltage and frequency under varying loads (m-36) Yearly Blackstart unit testing | Status Quo | Same as PJM (option A) | Generators will provide an annual confirmation whether governor frequency control capabilities should be available and largely unrestricted, to the extent it does not jeopardize unit reliability, during an actual system restoration event. Because system restoration is a manual, operationally intensive process, the TO, generator operator, and PJM will take into account governor droop settings, frequency control settings, and load reference settings (including headroom requirements) as applicable and consistent with the capabilities of generator in a manner that maintains both generator and island reliability. This manual mode of coordinated operation is to be expected to begin prior to generator synchronization and will likely remain until such time that the PJM marketplace and/or economic dispatch is restored. In the event a deficiency is identified from this annual data, (e.g. insufficient amount of units having operable governors capable of response during an actual restoration event) the TO and PJM can take alternative steps as identified in the system restoration plan. This could include the redirecting of paths to critical units capable of providing PFR during restoration or a new RFP process to seek incremental PFR capability in the area. See also "AEP PRF Package Clarification" - slides 1-3 | Status Quo | Status Quo
8 | Treatment of regulating units | Medium | Not defined | No performance assessment for PFR during hours unit is assigned regulation. No adjustment for regulation performance score. | Same as PJM (option A) | Same as PJM (option A) | No performance assessment for PFR during hours unit is assigned regulation. No adjustment for regulation performance score. | Same as PJM (option A)
9 | Treatment of pseudo tied or dynamically scheduled units | Medium | Not defined | Pseudo-tied resources must meet requirements above. Dynamically scheduled units follow rules of native BA. | Same as PJM (option A) | Same as PJM (option A) | Pseudo-tied resources must meet requirements above. Dynamically scheduled units follow rules of native BA. | Same as PJM (option A)
10 | Treatment of units providing synchronized reserve | Medium | Not defined | Expected to provide PFR | Same as PJM (option A) | Same as PJM (option A) | Expected to provide PFR | Same as PJM (option A)
11 | Treatment of CP units in Performance Assessment Interval | Medium | Not defined | PFR response would be accounted for in the Expected MW calculation during PAI | Same as PJM (option A) | Same as PJM (option A) | PFR response would be accounted for in the Expected MW calculation during PAI | Same as PJM (option A). Except, should be exemption from perfirmance when PEM is for a downward response b/c unit is providing "CP bonus payment" MWs
12 | Treatment of DER resources | Medium | Not defined | Wholesale DER subject to PFR requirements; Requirements to be documented in M-14D. For new resources, requirements apply to resources with ISA. | Same as PJM (option A) | DER resources that sign an ISA after October 1, 2018 will become obligated to provide PFR. | Wholesale DER subject to PFR requirements; Requirements to be documented in M-14D. For new resources, requirements apply to resources with ISA. | DER resources that sign an ISA or WMPA after October 1, 2018 will become obligated to provide PFR including "upward" PFR response.
13 | Treatment of load resources providing frequency response | Medium | Not defined | Status Quo | Same as PJM (option A) | Optional, but must provide appropriate telemetry to PJM to participate. | Status Quo | Optional, but must provide appropriate telemetry to PJM to participate.
14 | Implemenation Plan | High |  | 24 months from approved OATT and Manual requirements. Exception process for resources needing longer time to implement. PJM staff will provide quarterly updates to Operating Committee on PFR performance and trends. PJM staff will continue to follow industry and regulatory developments in PFR. PJM staff will consider PFR issues during restoration planning of the Black Start RFP. PFRSTF will go on hiatus for 9-12 months. PFRSTF will reconvene in the Fall/Winter of 2018 to review current status and discuss next steps. | Same as PJM (option A) | Upon FERC acceptance of appropriate tariff, or other PJM language. Stakeholders will reconvene if the PJM system-wide aggregate amount of PFR reduces by 10% or greater. This would indicate those currently providing are no longer providing. | 24 months from approved OATT and Manual requirements. Exception process for resources needing longer time to implement. PJM staff will provide quarterly updates to Operating Committee on PFR performance and trends. PJM staff will continue to follow industry and regulatory developments in PFR. PJM staff will consider PFR issues during restoration planning of the Black Start RFP. PFRSTF will go on hiatus for 9-12 months. PFRSTF will reconvene in the Fall/Winter of 2018 to review current status and discuss next steps. Stakeholders will reconvene if the PJM system-wide aggregate amount of PFR reduces by 10% or greater (generator performance or BAL-03 performance). This would indicate those currently providing are no longer providing. | Upon FERC acceptance of appropriate tariff, or other PJM language, Stakeholders will reconvene if the PJM system-wide aggregate amount of "up-direction" PFR reduces by 10% or greater. This would indicate those that were providing are no longer providing.
15 | Evaluate benefits of different resource types. Benefits factor | High | Not defined | Status Quo | Same as PJM (option A) | Same as PJM (option A) | Status Quo | Same as PJM (option A)
16 | Treatment of imbalance and operating reserve charges for units following basepoints for energy | High | PJM does not take into account the impact of following frequency for computation of energy imbalance and operating reserves | Frequency Response should fall within allowable basepoint bandwidth that is used to calculate whether or not units are following basepoints for Op Res calculation. (See tab 2b for details) Deviations from DA schedule would be settled at RT LMP. STATUS QUO | Same as PJM (option A) | Same as PJM (option A) | Frequency Response should fall within allowable basepoint bandwidth that is used to calculate whether or not units are following basepoints for Op Res calculation. (See tab 2b for details) Deviations from DA schedule would be settled at RT LMP. STATUS QUO | Same as PJM (option A)

## 3a. Package Details
PFRSTF
Primary Frequency Response Sr. Task Force
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
PFRSTF
Primary Frequency Response Sr. Task Force
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
PFRSTF
Primary Frequency Response Sr. Task Force
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3