## Instructions
Disclaimer
This is a simulation and interactive tool for memebers to use to understand their units performance
This tool is does not guarantee exact results to PJM calculations based on telemetry data but should provide a close estimate that will allow for futher discussion, if necessary.
Instructions
Step 1: | Enter is all unit information to set up template
All green colored cells need to entered by the user
**Data should be entered at 2 second granularity for the most accuracte calculation
| Unit Information: | Enter Unit Information here:
| Unit Name: | Enter Resource Name | Will be used to help PJM staff troubleshoot if data discrepancy is found
| MarketID: | Enter Units Makets Gateway ID | Will be used to help PJM staff troubleshoot if data discrepancy is found
| Frequency: | Low
| Regulation | Yes/No if unit is on for regulation | Used to determine expected MW of PFR response
| Eco Max: | Enter Unit's ECOMAX | Used in expected MW calculation
| Eco Min: | Enter Unit's ECOMIN | Used in expected MW calculation
| Zone | Enter Unit's Control Zone | Used for tracking purposes
| Fuel Type | Enter Unit's Fuel Type | Used for tracking purposes
| Governor Settings | Enter Governor Data here:
| Droop (%): | Enter unit's droop setting | Enter as a percent, set at 5% droop as default
| Deadband (Hz): | Enter unit's deadband setting | Enter as a decmial (field is in Hz), set at 0.036 Hz as default
| Plot Times | Enter Start Date/Time of Event here:
| Event Start: | Enter event start time (T0) | Will be used to calculated expected response and align frequency
| Plot Start: | 2017-11-20 16:11
| Plot End: | 2017-11-20 16:16
| Interval(seconds): | Enter Data sampling interval (2, 10, etc) | Used to set up data sampling table. 2sec samples are preferred if available
Step 2: | Enter in unit telemetry data for the set timestamps start in cell E43
All green colored cells need to entered by the user
Time | Frequency (Hz) | Unit Output (MW) | Eco Max (MW) | Eco Min (MW) | PFR Capacity (MW) | Expected Response (MW) | Expected Response Graph (Net MW) | Basepoint (MW) | Output Timestamp | Unit Output (MW)
Time Stamp | Enter Frequency Data | Enter Unit Output Data (MW) | calculated field 5% buffer on entered EcoMax for PFR calculation | calculated field 5% buffer on entered EcoMin for PFR calculation | calculated field PFR capability on unit | calculated field Expected Response based on Droop equation | calculated field total unit output expected based on droop equation | Enter Unit Basepoint (ECOBP) Data | Time Stamp | Enter Unit Output Data (MW)
Step 3: | Review Results
| Actual Response = | 0 | MW | Measured response at delta between -16-0 seconds and 20-52 seconds
| Expected Response = | 2.3728 | MW | Expected Response calculated as droop equation+ ramp rate
| Performance= | 0% | MW | Performance will be calculated based on Actual and Expected Response
|  | Fail |  | Pass/Fail assessment based on 50% performance score
| Ramp Rate | -0.016582 |  | Ramp Rate 1 minute before the event is calculated to offset expected response

## Event
Unit Information: | Enter Unit Information here:
Unit Name: | Resource123
MarketID: | 123
Frequency: | Low
Regulation | No | [13 empty] | X Axis
Eco Max: | 19 | [13 empty] | Stop | 43080.377
Eco Min: | 1 | [13 empty] | Y Axis
Zone | MidAtl
Fuel Type | Coal
Governor Settings | Enter Governor Data here: | Example Data | [12 empty] | MAX | 14
Droop (%): | 5% | 5% | [12 empty] | MIN | 2
Deadband (Hz): | 0.036 | 0.036 | [12 empty] | PointA
Plot Times | Enter Start Date/Time of Event here: | [12 empty] | 73 | 2017-12-11 08:59 | 14
Event Start: | 2017-12-11 08:59 | [13 empty] | 2017-12-11 08:59 | 2
Plot Start: | 2017-12-11 08:58 | [13 empty] | Point B
Plot End: | 2017-12-11 09:03 | [12 empty] | 91 | 2017-12-11 09:00 | 14
Interval(seconds): | 2 | [13 empty] | 2017-12-11 09:00 | 2
Unit Response (in MW) | Actual Resp. | Expected Resp.
Point A = | 0 | 0
Point B = | 0.24619 | 0.010661
Unit Output (in MW) | Actual Resp. | Expected Resp.
Point A = | 4.5354 | 4.5354
Point B = | 4.7816 | 4.6128
Actual Response = | 0.26277 | MW
Expected Response = | -0.0059212 | MW
Performance= | 0% | MW
Fail
Ramp Rate | -0.016582
[10 empty] | 0.0050329 | 4.5864 |  |  | 2017-12-11 08:49
|  |  |  | Time | Frequency (Hz) | Unit Output (MW) | Eco Max (MW) | Eco Min (MW) | PFR Capacity (MW) | Expected Response (MW) | Expected Response Graph (Net MW) | Basepoint (MW) | Output Timestamp | Unit Output (MW) | Regulation | Unit Ramp before Event (MW/min)
|  |  | 0 | 43080.3736 | 60.0162 | 4.5941 | 19 | 1 | 13.4559 | 0 | 4.5941 |  | 43080.3673 | 400 | No | 400 | MW-10min before
|  |  | 0 | 43080.3736 | 60.0165 | 4.6161 | 19 | 1 | 13.4339 | 0 | 4.6161 |  | 43080.3673 | 400 |  | 400 | MW- 0min before
|  |  | 0 | 43080.3736 | 60.0171 | 4.6381 | 19 | 1 | 13.4119 | 0 | 4.6381 |  | 43080.3674 | 400 |  | 0 | MW/min
|  |  | 0 | 43080.3736 | 60.0182 | 4.6601 | 19 | 1 | 13.3899 | 0 | 4.6601 |  | 43080.3674 | 400
|  |  | 0 | 43080.3737 | 60.0185 | 4.682 | 19 | 1 | 13.368 | 0 | 4.682 |  | 43080.3674 | 400
|  |  | 0 | 43080.3737 | 60.0185 | 4.704 | 19 | 1 | 13.346 | 0 | 4.704 |  | 43080.3674 | 400
|  |  | 0 | 43080.3737 | 60.0185 | 4.726 | 19 | 1 | 13.324 | 0 | 4.726 |  | 43080.3675 | 400
|  |  | 0 | 43080.3737 | 60.0179 | 4.748 | 19 | 1 | 13.302 | 0 | 4.748 |  | 43080.3675 | 400
|  |  | 0 | 43080.3738 | 60.017 | 4.759 | 19 | 1 | 13.291 | 0 | 4.759 |  | 43080.3675 | 400
|  |  | 0 | 43080.3738 | 60.017 | 4.7538 | 19 | 1 | 13.2962 | 0 | 4.7538 |  | 43080.3675 | 400
|  |  | 0 | 43080.3738 | 60.0166 | 4.7486 | 19 | 1 | 13.3014 | 0 | 4.7486 |  | 43080.3676 | 400
|  |  | 0 | 43080.3738 | 60.0156 | 4.7433 | 19 | 1 | 13.3067 | 0 | 4.7433 |  | 43080.3676 | 400
|  |  | 0 | 43080.3739 | 60.015 | 4.7381 | 19 | 1 | 13.3119 | 0 | 4.7381 |  | 43080.3676 | 400
|  |  | 0 | 43080.3739 | 60.0154 | 4.7329 | 19 | 1 | 13.3171 | 0 | 4.7329 |  | 43080.3676 | 400
|  |  | 0 | 43080.3739 | 60.016 | 4.7276 | 19 | 1 | 13.3224 | 0 | 4.7276 |  | 43080.3677 | 400
|  |  | 0 | 43080.3739 | 60.0156 | 4.7224 | 19 | 1 | 13.3276 | 0 | 4.7224 |  | 43080.3677 | 400
|  |  | 0 | 43080.3739 | 60.0152 | 4.7172 | 19 | 1 | 13.3328 | 0 | 4.7172 |  | 43080.3677 | 400
|  |  | 0 | 43080.374 | 60.0155 | 4.7119 | 19 | 1 | 13.3381 | 0 | 4.7119 |  | 43080.3677 | 400
|  |  | 0 | 43080.374 | 60.0153 | 4.7067 | 19 | 1 | 13.3433 | 0 | 4.7067 |  | 43080.3677 | 400
|  |  | 0 | 43080.374 | 60.015 | 4.7015 | 19 | 1 | 13.3485 | 0 | 4.7015 |  | 43080.3678 | 400
|  |  | 0 | 43080.374 | 60.0156 | 4.6962 | 19 | 1 | 13.3538 | 0 | 4.6962 |  | 43080.3678 | 400
|  |  | 0 | 43080.3741 | 60.0165 | 4.691 | 19 | 1 | 13.359 | 0 | 4.691 |  | 43080.3678 | 400
|  |  | 0 | 43080.3741 | 60.0167 | 4.6143 | 19 | 1 | 13.4357 | 0 | 4.6143 |  | 43080.3678 | 400
|  |  | 0 | 43080.3741 | 60.0168 | 4.5079 | 19 | 1 | 13.5421 | 0 | 4.5079 |  | 43080.3679 | 400
|  |  | 0 | 43080.3741 | 60.0165 | 4.5157 | 19 | 1 | 13.5343 | 0 | 4.5157 |  | 43080.3679 | 400
|  |  | 0 | 43080.3742 | 60.0159 | 4.5236 | 19 | 1 | 13.5264 | 0 | 4.5236 |  | 43080.3679 | 400
|  |  | 0 | 43080.3742 | 60.015 | 4.5314 | 19 | 1 | 13.5186 | 0 | 4.5314 |  | 43080.3679 | 400
|  |  | 0 | 43080.3742 | 60.0144 | 4.5393 | 19 | 1 | 13.5107 | 0 | 4.5393 |  | 43080.368 | 400
Expected | Actual |  | 0 | 43080.3742 | 60.0129 | 4.5471 | 19 | 1 | 13.5029 | 0 | 4.5471 |  | 43080.368 | 400
Point A |  |  | 0 | 43080.3742 | 60.012 | 4.555 | 19 | 1 | 13.495 | 0 | 4.555 |  | 43080.368 | 400
4.5354 | 4.5354 | MW output | 0 | 43080.3743 | 60.0009 | 4.5628 | 19 | 1 | 13.4872 | 0 | 4.5628 |  | 43080.368 | 400
0 | 0 | PFR expected | 0 | 43080.3743 | 59.9845 | 4.5707 | 19 | 1 | 13.4793 | 0 | 4.5707 |  | 43080.368 | 400
66 | 2017-12-11 08:59 |  | 0 | 43080.3743 | 59.9772 | 4.5786 | 19 | 1 | 13.4714 | 0 | 4.5786 |  | 43080.3681 | 400
73 | 2017-12-11 08:59 |  | 0.0050329 | 43080.3743 | 59.9632 | 4.5864 | 19 | 1 | 13.4636 | 0.0050329 | 4.5914 |  | 43080.3681 | 400
|  |  | 0.034597 | 43080.3744 | 59.9586 | 4.5943 | 19 | 1 | 13.4557 | 0.034597 | 4.621 |  | 43080.3681 | 400
|  |  | 0.03846 | 43080.3744 | 59.958 | 4.6021 | 19 | 1 | 13.4479 | 0.03846 | 4.6249 |  | 43080.3681 | 400
|  |  | 0.03846 | 43080.3744 | 59.958 | 4.61 | 19 | 1 | 13.44 | 0.03846 | 4.6249 |  | 43080.3682 | 400
|  |  | 0.03846 | 43080.3744 | 59.958 | 4.7179 | 19 | 1 | 13.3321 | 0.03846 | 4.6249 |  | 43080.3682 | 400
|  |  | 0.032054 | 43080.3745 | 59.959 | 4.871 | 19 | 1 | 13.179 | 0.032054 | 4.6185 |  | 43080.3682 | 400
|  |  | 0.02374 | 43080.3745 | 59.9603 | 4.871 | 19 | 1 | 13.179 | 0.02374 | 4.6101 |  | 43080.3682 | 400
Point B |  |  | 0.020512 | 43080.3745 | 59.9608 | 4.871 | 19 | 1 | 13.179 | 0.020512 | 4.6069 |  | 43080.3683 | 400
4.6128 | 4.7816 | MW output | 0.012809 | 43080.3745 | 59.962 | 4.871 | 19 | 1 | 13.179 | 0.012809 | 4.5992 |  | 43080.3683 | 400
0.010661 | 0.24619 | PFR expected | 0.012809 | 43080.3745 | 59.962 | 4.7821 | 19 | 1 | 13.2679 | 0.012809 | 4.5992 |  | 43080.3683 | 400
83 | 2017-12-11 08:59 |  | 0.012809 | 43080.3746 | 59.962 | 4.6512 | 19 | 1 | 13.3988 | 0.012809 | 4.5992 |  | 43080.3683 | 400
99 | 2017-12-11 09:00 |  | 0.0076983 | 43080.3746 | 59.9628 | 4.6512 | 19 | 1 | 13.3988 | 0.0076983 | 4.5941 |  | 43080.3683 | 400
|  |  | 0 | 43080.3746 | 59.964 | 4.6512 | 19 | 1 | 13.3988 | 0 | 4.6512 |  | 43080.3684 | 400
|  |  | 0 | 43080.3746 | 59.964 | 4.6512 | 19 | 1 | 13.3988 | 0 | 4.6512 |  | 43080.3684 | 400
|  |  | 0 | 43080.3747 | 59.964 | 4.7243 | 19 | 1 | 13.3257 | 0 | 4.7243 |  | 43080.3684 | 400
|  |  | 0.0050573 | 43080.3747 | 59.9632 | 4.8336 | 19 | 1 | 13.2164 | 0.0050573 | 4.5915 |  | 43080.3684 | 400
|  |  | 0.012809 | 43080.3747 | 59.962 | 4.8317 | 19 | 1 | 13.2183 | 0.012809 | 4.5992 |  | 43080.3685 | 400
|  |  | 0.014081 | 43080.3747 | 59.9618 | 4.8298 | 19 | 1 | 13.2202 | 0.014081 | 4.6005 |  | 43080.3685 | 400
|  |  | 0.016012 | 43080.3748 | 59.9615 | 4.8278 | 19 | 1 | 13.2222 | 0.016012 | 4.6024 |  | 43080.3685 | 400
|  |  | 0.016012 | 43080.3748 | 59.9615 | 4.8259 | 19 | 1 | 13.2241 | 0.016012 | 4.6024 |  | 43080.3685 | 400
|  |  | 0.016012 | 43080.3748 | 59.9615 | 4.824 | 19 | 1 | 13.226 | 0.016012 | 4.6024 |  | 43080.3686 | 400
|  |  | 0.016012 | 43080.3748 | 59.9615 | 4.822 | 19 | 1 | 13.228 | 0.016012 | 4.6024 |  | 43080.3686 | 400
|  |  | 0.012198 | 43080.3748 | 59.9621 | 4.8201 | 19 | 1 | 13.2299 | 0.012198 | 4.5986 |  | 43080.3686 | 400
|  |  | 0.0064022 | 43080.3749 | 59.963 | 4.8182 | 19 | 1 | 13.2318 | 0.0064022 | 4.5928 |  | 43080.3686 | 400
|  |  | 0.0064022 | 43080.3749 | 59.963 | 4.8163 | 19 | 1 | 13.2337 | 0.0064022 | 4.5928 |  | 43080.3686 | 400
|  |  | 0.0076738 | 43080.3749 | 59.9628 | 4.8143 | 19 | 1 | 13.2357 | 0.0076738 | 4.5941 |  | 43080.3687 | 400
|  |  | 0.010877 | 43080.3749 | 59.9623 | 4.8124 | 19 | 1 | 13.2376 | 0.010877 | 4.5973 |  | 43080.3687 | 400
|  |  | 0.010241 | 43080.375 | 59.9624 | 4.8105 | 19 | 1 | 13.2395 | 0.010241 | 4.5966 |  | 43080.3687 | 400
|  |  | 0.0064022 | 43080.375 | 59.963 | 4.8085 | 19 | 1 | 13.2415 | 0.0064022 | 4.5928 |  | 43080.3687 | 400
|  |  | 0.0051307 | 43080.375 | 59.9632 | 4.8066 | 19 | 1 | 13.2434 | 0.0051307 | 4.5915 |  | 43080.3688 | 400
|  |  | 0.0031989 | 43080.375 | 59.9635 | 4.8047 | 19 | 1 | 13.2453 | 0.0031989 | 4.5896 |  | 43080.3688 | 400
|  |  | 0.0096056 | 43080.3751 | 59.9625 | 4.8027 | 19 | 1 | 13.2473 | 0.0096056 | 4.596 |  | 43080.3688 | 400
|  |  | 0.01924 | 43080.3751 | 59.961 | 4.8008 | 19 | 1 | 13.2492 | 0.01924 | 4.6056 |  | 43080.3688 | 400
|  |  | 0.01924 | 43080.3751 | 59.961 | 4.7989 | 19 | 1 | 13.2511 | 0.01924 | 4.6056 |  | 43080.3689 | 400
|  |  | 0.01924 | 43080.3751 | 59.961 | 4.8718 | 19 | 1 | 13.1782 | 0.01924 | 4.6056 |  | 43080.3689 | 400
|  |  | 0.016648 | 43080.3752 | 59.9614 | 4.9809 | 19 | 1 | 13.0691 | 0.016648 | 4.6031 |  | 43080.3689 | 400
|  |  | 0.011537 | 43080.3752 | 59.9622 | 4.9809 | 19 | 1 | 13.0691 | 0.011537 | 4.5979 |  | 43080.3689 | 400
|  |  | 0.0083096 | 43080.3752 | 59.9627 | 4.9809 | 19 | 1 | 13.0691 | 0.0083096 | 4.5947 |  | 43080.3689 | 400
|  |  | 0.0064022 | 43080.3752 | 59.963 | 4.9809 | 19 | 1 | 13.0691 | 0.0064022 | 4.5928 |  | 43080.369 | 400
|  |  | 0.0038591 | 43080.3752 | 59.9634 | 5.3143 | 19 | 1 | 12.7357 | 0.0038591 | 4.5903 |  | 43080.369 | 400
|  |  | 0 | 43080.3753 | 59.964 | 5.8232 | 19 | 1 | 12.2268 | 0 | 5.8232 |  | 43080.369 | 400
|  |  | 0 | 43080.3753 | 59.964 | 5.8232 | 19 | 1 | 12.2268 | 0 | 5.8232 |  | 43080.369 | 400
|  |  | 0 | 43080.3753 | 59.9644 | 5.8232 | 19 | 1 | 12.2268 | 0 | 5.8232 |  | 43080.3691 | 400
|  |  | 0 | 43080.3753 | 59.965 | 5.8232 | 19 | 1 | 12.2268 | 0 | 5.8232 |  | 43080.3691 | 400
|  |  | 0 | 43080.3754 | 59.9652 | 5.764 | 19 | 1 | 12.286 | 0 | 5.764 |  | 43080.3691 | 400
|  |  | 0 | 43080.3754 | 59.9653 | 5.68 | 19 | 1 | 12.37 | 0 | 5.68 |  | 43080.3691 | 400
|  |  | 0 | 43080.3754 | 59.965 | 5.6881 | 19 | 1 | 12.3619 | 0 | 5.6881 |  | 43080.3692 | 400
|  |  | 0 | 43080.3754 | 59.9656 | 5.6963 | 19 | 1 | 12.3537 | 0 | 5.6963 |  | 43080.3692 | 400
|  |  | 0 | 43080.3755 | 59.9665 | 5.7044 | 19 | 1 | 12.3456 | 0 | 5.7044 |  | 43080.3692 | 400
|  |  | 0 | 43080.3755 | 59.9673 | 5.7125 | 19 | 1 | 12.3375 | 0 | 5.7125 |  | 43080.3692 | 400
|  |  | 0 | 43080.3755 | 59.9683 | 5.7207 | 19 | 1 | 12.3293 | 0 | 5.7207 |  | 43080.3692 | 400
|  |  | 0 | 43080.3755 | 59.968 | 5.7288 | 19 | 1 | 12.3212 | 0 | 5.7288 |  | 43080.3693 | 400
|  |  | 0 | 43080.3755 | 59.9684 | 5.737 | 19 | 1 | 12.313 | 0 | 5.737 |  | 43080.3693 | 400
|  |  | 0 | 43080.3756 | 59.969 | 5.7451 | 19 | 1 | 12.3049 | 0 | 5.7451 |  | 43080.3693 | 400
|  |  | 0 | 43080.3756 | 59.969 | 5.5731 | 19 | 1 | 12.4769 | 0 | 5.5731 |  | 43080.3693 | 400
|  |  | 0 | 43080.3756 | 59.9694 | 5.3105 | 19 | 1 | 12.7395 | 0 | 5.3105 |  | 43080.3694 | 400
|  |  | 0 | 43080.3756 | 59.9698 | 5.3105 | 19 | 1 | 12.7395 | 0 | 5.3105 |  | 43080.3694 | 400
|  |  | 0 | 43080.3757 | 59.9693 | 5.3105 | 19 | 1 | 12.7395 | 0 | 5.3105 |  | 43080.3694 | 400
|  |  | 0 | 43080.3757 | 59.969 | 5.3105 | 19 | 1 | 12.7395 | 0 | 5.3105 |  | 43080.3694 | 400
|  |  | 0 | 43080.3757 | 59.9684 | 5.2376 | 19 | 1 | 12.8124 | 0 | 5.2376 |  | 43080.3695 | 400
|  |  | 0 | 43080.3757 | 59.9671 | 5.1274 | 19 | 1 | 12.9226 | 0 | 5.1274 |  | 43080.3695 | 400
|  |  | 0 | 43080.3758 | 59.9667 | 5.1274 | 19 | 1 | 12.9226 | 0 | 5.1274 |  | 43080.3695 | 400
|  |  | 0 | 43080.3758 | 59.967 | 5.1274 | 19 | 1 | 12.9226 | 0 | 5.1274 |  | 43080.3695 | 400
|  |  | 0 | 43080.3758 | 59.9676 | 5.1274 | 19 | 1 | 12.9226 | 0 | 5.1274 |  | 43080.3695 | 400
|  |  | 0 | 43080.3758 | 59.9689 | 5.0548 | 19 | 1 | 12.9952 | 0 | 5.0548 |  | 43080.3696 | 400
|  |  | 0 | 43080.3758 | 59.9695 | 4.9442 | 19 | 1 | 13.1058 | 0 | 4.9442 |  | 43080.3696 | 400
|  |  | 0 | 43080.3759 | 59.9699 | 4.9442 | 19 | 1 | 13.1058 | 0 | 4.9442 |  | 43080.3696 | 400
|  |  | 0 | 43080.3759 | 59.9705 | 4.9442 | 19 | 1 | 13.1058 | 0 | 4.9442 |  | 43080.3696 | 400
|  |  | 0 | 43080.3759 | 59.9703 | 4.9442 | 19 | 1 | 13.1058 | 0 | 4.9442 |  | 43080.3697 | 400
|  |  | 0 | 43080.3759 | 59.97 | 4.8714 | 19 | 1 | 13.1786 | 0 | 4.8714 |  | 43080.3697 | 400
|  |  | 0 | 43080.376 | 59.9702 | 4.7611 | 19 | 1 | 13.2889 | 0 | 4.7611 |  | 43080.3697 | 400
|  |  | 0 | 43080.376 | 59.9705 | 4.7611 | 19 | 1 | 13.2889 | 0 | 4.7611 |  | 43080.3697 | 400
|  |  | 0 | 43080.376 | 59.9709 | 4.7611 | 19 | 1 | 13.2889 | 0 | 4.7611 |  | 43080.3698 | 400
|  |  | 0 | 43080.376 | 59.9719 | 4.7611 | 19 | 1 | 13.2889 | 0 | 4.7611 |  | 43080.3698 | 400
|  |  | 0 | 43080.3761 | 59.9735 | 5.4064 | 19 | 1 | 12.6436 | 0 | 5.4064 |  | 43080.3698 | 400
|  |  | 0 | 43080.3761 | 59.9748 | 6.3726 | 19 | 1 | 11.6774 | 0 | 6.3726 |  | 43080.3698 | 400
|  |  | 0 | 43080.3761 | 59.9745 | 6.3726 | 19 | 1 | 11.6774 | 0 | 6.3726 |  | 43080.3698 | 400
|  |  | 0 | 43080.3761 | 59.9739 | 6.3726 | 19 | 1 | 11.6774 | 0 | 6.3726 |  | 43080.3699 | 400
|  |  | 0 | 43080.3761 | 59.9726 | 6.3726 | 19 | 1 | 11.6774 | 0 | 6.3726 |  | 43080.3699 | 400
|  |  | 0 | 43080.3762 | 59.9718 | 6.6243 | 19 | 1 | 11.4257 | 0 | 6.6243 |  | 43080.3699 | 400
|  |  | 0 | 43080.3762 | 59.9713 | 6.9952 | 19 | 1 | 11.0548 | 0 | 6.9952 |  | 43080.3699 | 400
|  |  | 0 | 43080.3762 | 59.971 | 6.9952 | 19 | 1 | 11.0548 | 0 | 6.9952 |  | 43080.37 | 400
|  |  | 0 | 43080.3762 | 59.9716 | 6.9952 | 19 | 1 | 11.0548 | 0 | 6.9952 |  | 43080.37 | 400
|  |  | 0 | 43080.3763 | 59.9727 | 6.9952 | 19 | 1 | 11.0548 | 0 | 6.9952 |  | 43080.37 | 400
|  |  | 0 | 43080.3763 | 59.9726 | 7.2572 | 19 | 1 | 10.7928 | 0 | 7.2572 |  | 43080.37 | 400
|  |  | 0 | 43080.3763 | 59.9716 | 7.6544 | 19 | 1 | 10.3956 | 0 | 7.6544 |  | 43080.3701 | 400
|  |  | 0 | 43080.3763 | 59.971 | 7.6544 | 19 | 1 | 10.3956 | 0 | 7.6544 |  | 43080.3701 | 400
|  |  | 0 | 43080.3764 | 59.9698 | 7.6544 | 19 | 1 | 10.3956 | 0 | 7.6544 |  | 43080.3701 | 400
|  |  | 0 | 43080.3764 | 59.968 | 7.6544 | 19 | 1 | 10.3956 | 0 | 7.6544 |  | 43080.3701 | 400
|  |  | 0 | 43080.3764 | 59.9674 | 7.7995 | 19 | 1 | 10.2505 | 0 | 7.7995 |  | 43080.3702 | 400
|  |  | 0 | 43080.3764 | 59.9665 | 8.0207 | 19 | 1 | 10.0293 | 0 | 8.0207 |  | 43080.3702 | 400
|  |  | 0 | 43080.3764 | 59.9663 | 8.0207 | 19 | 1 | 10.0293 | 0 | 8.0207 |  | 43080.3702 | 400
|  |  | 0 | 43080.3765 | 59.9656 | 8.0207 | 19 | 1 | 10.0293 | 0 | 8.0207 |  | 43080.3702 | 400
|  |  | 0 | 43080.3765 | 59.965 | 8.0207 | 19 | 1 | 10.0293 | 0 | 8.0207 |  | 43080.3702 | 400
|  |  | 0 | 43080.3765 | 59.9642 | 8.2257 | 19 | 1 | 9.8243 | 0 | 8.2257 |  | 43080.3703 | 400
|  |  | 0.0089454 | 43080.3765 | 59.9626 | 8.5334 | 19 | 1 | 9.5166 | 0.0089454 | 4.5953 |  | 43080.3703 | 400
|  |  | 0.012809 | 43080.3766 | 59.962 | 8.5334 | 19 | 1 | 9.5166 | 0.012809 | 4.5992 |  | 43080.3703 | 400
|  |  | 0.012809 | 43080.3766 | 59.962 | 8.5334 | 19 | 1 | 9.5166 | 0.012809 | 4.5992 |  | 43080.3703 | 400
|  |  | 0.014081 | 43080.3766 | 59.9618 | 8.5334 | 19 | 1 | 9.5166 | 0.014081 | 4.6005 |  | 43080.3704 | 400
|  |  | 0.014741 | 43080.3766 | 59.9617 | 8.735 | 19 | 1 | 9.315 | 0.014741 | 4.6011 |  | 43080.3704 | 400
|  |  | 0.015377 | 43080.3767 | 59.9616 | 9.0461 | 19 | 1 | 9.0039 | 0.015377 | 4.6018 |  | 43080.3704 | 400
|  |  | 0.01924 | 43080.3767 | 59.961 | 9.0461 | 19 | 1 | 9.0039 | 0.01924 | 4.6056 |  | 43080.3704 | 400
|  |  | 0.021783 | 43080.3767 | 59.9606 | 9.0461 | 19 | 1 | 9.0039 | 0.021783 | 4.6082 |  | 43080.3705 | 400
|  |  | 0.029486 | 43080.3767 | 59.9594 | 9.0461 | 19 | 1 | 9.0039 | 0.029486 | 4.6159 |  | 43080.3705 | 400
|  |  | 0.036529 | 43080.3767 | 59.9583 | 9.2207 | 19 | 1 | 8.8293 | 0.036529 | 4.6229 |  | 43080.3705 | 400
|  |  | 0.037189 | 43080.3768 | 59.9582 | 9.4856 | 19 | 1 | 8.5644 | 0.037189 | 4.6236 |  | 43080.3705 | 400
|  |  | 0.036529 | 43080.3768 | 59.9583 | 9.4856 | 19 | 1 | 8.5644 | 0.036529 | 4.6229 |  | 43080.3705 | 400
|  |  | 0.030733 | 43080.3768 | 59.9592 | 9.4856 | 19 | 1 | 8.5644 | 0.030733 | 4.6171 |  | 43080.3706 | 400
|  |  | 0.014056 | 43080.3768 | 59.9618 | 9.4856 | 19 | 1 | 8.5644 | 0.014056 | 4.6005 |  | 43080.3706 | 400
|  |  | 0.0038347 | 43080.3769 | 59.9634 | 9.5741 | 19 | 1 | 8.4759 | 0.0038347 | 4.5902 |  | 43080.3706 | 400
|  |  | 0 | 43080.3769 | 59.9646 | 9.7054 | 19 | 1 | 8.3446 | 0 | 9.7054 |  | 43080.3706 | 400
|  |  | 0 | 43080.3769 | 59.9657 | 9.7054 | 19 | 1 | 8.3446 | 0 | 9.7054 |  | 43080.3707 | 400
|  |  | 0 | 43080.3769 | 59.9664 | 9.7054 | 19 | 1 | 8.3446 | 0 | 9.7054 |  | 43080.3707 | 400
|  |  | 0 | 43080.377 | 59.9674 | 9.7054 | 19 | 1 | 8.3446 | 0 | 9.7054 |  | 43080.3707 | 400
|  |  | 0 | 43080.377 | 59.9682 | 10.2498 | 19 | 1 | 7.8002 | 0 | 10.2498 |  | 43080.3707 | 400
|  |  | 0 | 43080.377 | 59.9685 | 11.0971 | 19 | 1 | 6.9529 | 0 | 11.0971 |  | 43080.3708 | 400
|  |  | 0 | 43080.377 | 59.9685 | 11.0971 | 19 | 1 | 6.9529 | 0 | 11.0971 |  | 43080.3708 | 400
|  |  | 0 | 43080.377 | 59.9691 | 11.0971 | 19 | 1 | 6.9529 | 0 | 11.0971 |  | 43080.3708 | 400
[13 empty] | 43080.3708 | 400
[13 empty] | 43080.3708 | 400
[13 empty] | 43080.3709 | 400
[13 empty] | 43080.3709 | 400
[13 empty] | 43080.3709 | 400
[13 empty] | 43080.3709 | 400
[13 empty] | 43080.371 | 400
[13 empty] | 43080.371 | 400
[13 empty] | 43080.371 | 400
[13 empty] | 43080.371 | 400
[13 empty] | 43080.3711 | 400
[13 empty] | 43080.3711 | 400
[13 empty] | 43080.3711 | 400
[13 empty] | 43080.3711 | 400
[13 empty] | 43080.3711 | 400
[13 empty] | 43080.3712 | 400
[13 empty] | 43080.3712 | 400
[13 empty] | 43080.3712 | 400
[13 empty] | 43080.3712 | 400
[13 empty] | 43080.3713 | 400
[13 empty] | 43080.3713 | 400
[13 empty] | 43080.3713 | 400
[13 empty] | 43080.3713 | 400
[13 empty] | 43080.3714 | 400
[13 empty] | 43080.3714 | 400
[13 empty] | 43080.3714 | 400
[13 empty] | 43080.3714 | 400
[13 empty] | 43080.3714 | 400
[13 empty] | 43080.3715 | 400
[13 empty] | 43080.3715 | 400
[13 empty] | 43080.3715 | 400
[13 empty] | 43080.3715 | 400
[13 empty] | 43080.3716 | 400
[13 empty] | 43080.3716 | 400
[13 empty] | 43080.3716 | 400
[13 empty] | 43080.3716 | 400
[13 empty] | 43080.3717 | 400
[13 empty] | 43080.3717 | 400
[13 empty] | 43080.3717 | 400
[13 empty] | 43080.3717 | 400
[13 empty] | 43080.3717 | 400
[13 empty] | 43080.3718 | 400
[13 empty] | 43080.3718 | 400
[13 empty] | 43080.3718 | 400
[13 empty] | 43080.3718 | 400
[13 empty] | 43080.3719 | 400
[13 empty] | 43080.3719 | 400
[13 empty] | 43080.3719 | 400
[13 empty] | 43080.3719 | 400
[13 empty] | 43080.372 | 400
[13 empty] | 43080.372 | 400
[13 empty] | 43080.372 | 400
[13 empty] | 43080.372 | 400
[13 empty] | 43080.372 | 400
[13 empty] | 43080.3721 | 400
[13 empty] | 43080.3721 | 400
[13 empty] | 43080.3721 | 400
[13 empty] | 43080.3721 | 400
[13 empty] | 43080.3722 | 400
[13 empty] | 43080.3722 | 400
[13 empty] | 43080.3722 | 400
[13 empty] | 43080.3722 | 400
[13 empty] | 43080.3723 | 400
[13 empty] | 43080.3723 | 400
[13 empty] | 43080.3723 | 400
[13 empty] | 43080.3723 | 400
[13 empty] | 43080.3723 | 400
[13 empty] | 43080.3724 | 400
[13 empty] | 43080.3724 | 400
[13 empty] | 43080.3724 | 400
[13 empty] | 43080.3724 | 400
[13 empty] | 43080.3725 | 400
[13 empty] | 43080.3725 | 400
[13 empty] | 43080.3725 | 400
[13 empty] | 43080.3725 | 400
[13 empty] | 43080.3726 | 400
[13 empty] | 43080.3726 | 400
[13 empty] | 43080.3726 | 400
[13 empty] | 43080.3726 | 400
[13 empty] | 43080.3727 | 400
[13 empty] | 43080.3727 | 400
[13 empty] | 43080.3727 | 400
[13 empty] | 43080.3727 | 400
[13 empty] | 43080.3727 | 400
[13 empty] | 43080.3728 | 400
[13 empty] | 43080.3728 | 400
[13 empty] | 43080.3728 | 400
[13 empty] | 43080.3728 | 400
[13 empty] | 43080.3729 | 400
[13 empty] | 43080.3729 | 400
[13 empty] | 43080.3729 | 400
[13 empty] | 43080.3729 | 400
[13 empty] | 43080.373 | 400
[13 empty] | 43080.373 | 400
[13 empty] | 43080.373 | 400
[13 empty] | 43080.373 | 400
[13 empty] | 43080.373 | 400
[13 empty] | 43080.3731 | 400
[13 empty] | 43080.3731 | 400
[13 empty] | 43080.3731 | 400
[13 empty] | 43080.3731 | 400
[13 empty] | 43080.3732 | 400
[13 empty] | 43080.3732 | 400
[13 empty] | 43080.3732 | 400
[13 empty] | 43080.3732 | 400
[13 empty] | 43080.3733 | 400
[13 empty] | 43080.3733 | 400
[13 empty] | 43080.3733 | 400
[13 empty] | 43080.3733 | 400
[13 empty] | 43080.3733 | 400
[13 empty] | 43080.3734 | 400
[13 empty] | 43080.3734 | 400
[13 empty] | 43080.3734 | 400
[13 empty] | 43080.3734 | 400
[13 empty] | 43080.3735 | 400
[13 empty] | 43080.3735 | 400
[13 empty] | 43080.3735 | 400
[13 empty] | 43080.3735 | 400
[13 empty] | 43080.3736 | 400
[13 empty] | 43080.3736 | 400
[13 empty] | 43080.3736 | 400
[13 empty] | 43080.3736 | 400
[13 empty] | 43080.3736 | 400
[13 empty] | 43080.3737 | 400
[13 empty] | 43080.3737 | 400
[13 empty] | 43080.3737 | 400
[13 empty] | 43080.3737 | 400
[13 empty] | 43080.3738 | 400
[13 empty] | 43080.3738 | 400
[13 empty] | 43080.3738 | 400
[13 empty] | 43080.3738 | 400
[13 empty] | 43080.3739 | 400
[13 empty] | 43080.3739 | 400
[13 empty] | 43080.3739 | 400
[13 empty] | 43080.3739 | 400
[13 empty] | 43080.3739 | 400
[13 empty] | 43080.374 | 400
[13 empty] | 43080.374 | 400
[13 empty] | 43080.374 | 400
[13 empty] | 43080.374 | 400
[13 empty] | 43080.3741 | 400
[13 empty] | 43080.3741 | 400
[13 empty] | 43080.3741 | 400
[13 empty] | 43080.3741 | 400
[13 empty] | 43080.3742 | 400
[13 empty] | 43080.3742 | 400
[13 empty] | 43080.3742 | 400
[13 empty] | 43080.3742 | 400
[13 empty] | 43080.3742 | 400
[13 empty] | 43080.3743 | 400
Formulas:
X Axis = [No, row below]
X Axis = [No]
No = [No, row above]-TIME(0,1,0)
Set Plot

## Sheet1
2017-12-11 08:58 | 2017-12-11 08:58 | 60.0175 | 60.0032
2017-12-11 09:03 | 2017-12-11 08:58 | 60.0176 | 60.0015
10s | 2017-12-11 08:58 | 60.0156 | 60.0015
| 2017-12-11 08:58 | 60.0153 | 60.0047
ca_rt_fq/pjmc:freq-agc freq:hz | 2017-12-11 08:59 | 60.0165 | 60.0011
| 2017-12-11 08:59 | 60.0132 | 60.0004
| 2017-12-11 08:59 | 59.9719 | 59.9818
| 2017-12-11 08:59 | 59.9589 | 59.9493
| 2017-12-11 08:59 | 59.9623 | 59.9526
| 2017-12-11 08:59 | 59.9632 | 59.9489
| 2017-12-11 09:00 | 59.9615 | 59.9517
| 2017-12-11 09:00 | 59.9627 | 59.9515
| 2017-12-11 09:00 | 59.9628 | 59.95
| 2017-12-11 09:00 | 59.9615 | 59.947
| 2017-12-11 09:00 | 59.9636 | 59.9485
| 2017-12-11 09:00 | 59.9651 | 59.9505
| 2017-12-11 09:01 | 59.9674 | 59.9527
| 2017-12-11 09:01 | 59.9692 | 59.9528
| 2017-12-11 09:01 | 59.9679 | 59.954
| 2017-12-11 09:01 | 59.9689 | 59.9557
| 2017-12-11 09:01 | 59.9703 | 59.9608
| 2017-12-11 09:01 | 59.9735 | 59.9655
| 2017-12-11 09:02 | 59.9718 | 59.9662
| 2017-12-11 09:02 | 59.9718 | 59.9735
| 2017-12-11 09:02 | 59.9671 | 59.9804
| 2017-12-11 09:02 | 59.9635 | 59.9843
| 2017-12-11 09:02 | 59.9615 | 59.991
| 2017-12-11 09:02 | 59.9587 | 59.9944
| 2017-12-11 09:03 | 59.9637 | 59.9944
| 2017-12-11 09:03 | 59.9681 | 60