## Schedule 1
Reactive Supply and Voltage Control - Template |  |  |  |  | Exhibit No._____
Fixed Capability Revenue Requirement |  |  |  |  | Schedule 1
Line No. | Item | Source | Amount | Amount | Amount
(A) | (B) | (C) | (D) | (D-1) | (D-2)
|  |  |  | 100MWac (130MWdc) Solar Proxy | 100 MWac Wind Proxy
Reactive Production Investment (Generator Exciter [Inverters][Turbine Generator/Converters]) (Note A)
1 | Capital Cost of Generator/Exciter [Inverters][Turbine Generator/Converters] | EPC Estimate | 0 | 7475000 | 130769600
2 | Turbine Generator/Converter/Controller Allocator | Estimate |  | N/A | 10.06%
3 | Power Factor | Standard Equipment Ratings | 1 | 0.8 | 0.907
4 | Reactive Allocation Factor (1-PF^2) | 1-D3^2 | 0% | 36% | 17.74%
5 | Total Investment in Reactive Power (Inverters) | D1*D2*D4 | 0 | 2691000 | 2333127.2046
6
7 | Reactive Production Investment (Step-up Transformer / GSU) (Note A)
8 | Capital Cost of Step-up Transformers [GSU] | EPC Estimate | 0 | 6448000 | 1724800
9 | Reactive Allocation Factor (1-PF^2) | 1-D3^2 | 0% | 36% | 17.74%
10 | Total Investment in Reactive Power (Step-up Transformer [GSU]) | D8*D9 | 0 | 2321280 | 305895.0048
11
12 | Reactive Production Investment (Accessory Electric Equipment - DC System)
13 | Total Capital Cost of Accessory Electric Equipment - DC System | EPC Estimate | 0 | 4485000 | 0
14 | AEE Allocator - DC System |  | 10% | 10% | 10%
15 | Reactive Allocation Factor | 1-D3^2 | 0% | 36% | 17.74%
16 | Total Investment in Reactive Power (Accessory Electric Equipment - DC System) | D13*D14*D15 | 0 | 161460 | 0
17
18 | Reactive Production Investment (Accessory Electric Equipment - AC System)
19 | Total Capital Cost of Accessory Electric Equipment - AC System | EPC Estimate | 0 | 4082000 | 10706100
20 | AEE Allocator - AC System |  | 100% | 86.34% | 86.34%
21 | Reactive Allocation Factor | 1-D3^2 | 0% | 36% | 17.74%
22 | Total Investment in Reactive Power (Accessory Electric Equipment - AC System) | D19*D20*D21 | 0 | 1268783.568 | 1639369.993
23
24 | Reactive Production Investment (Accessory Electric Equipment - Capacitor Banks) | EPC Estimate | 0 | 0 | 447210.719
25
26 | Reactive Production Equipment (Balance of Plant)
27 | Total Capital Cost of Balance of Plant | EPC Estimate | 0 | 124956000 | 148242200
28 | Balance of Plant Allocator | AEP Allocator | 0.15% | 0.15% | 0.15%
29 | Total Investment in Reactive Power (Balance of Plant) | D27*D28 | 0 | 187434 | 222363.3
30
31 | Total Plant Cost of Reactive Power Producing Facilities | D5+D10+D16+D22+D24+D29 | 0 | 6629957.568 | 4947966.2213
32
33 | Total Annual Fixed Charge Carrying Rate | Schedule 1 - FCR Estimate | 0% | 11.62% | 11.78%
34
35 | Total Annual Fixed Capability Revenue Requirement (Note B) | D31*D33 | 0 | 770632.0586 | 582632.4359
36 | Total Monthly Fixed Capability Revenue Requirement (Note B) | D35/12 | 0 | 64219.3382 | 48552.703
Notes: |  | $ / kW-mo | 0 | 0.64219 | 0.48553

## Schedule 1 - FCR Estimate
Reactive Supply and Voltage Control - Template | [5 empty] | Exhibit No._____
Annual Fixed Carrying Charge | [5 empty] | Schedule 1
Attachment FCR
Line No. | Item | Source | Percent | Rate | Amount | Rate
(A) | (B) | (C) | (D) | (E) | (F) | (G)
1
2 | Fixed Operating Expenses Rate - Solar | EPC Estimate - OpEx / CapEx |  |  |  | 2%
3
4 | Depreciation Expense Rate (SLD=1/n) - Solar | 1/F5 | 5%
5 | 1 / Straight-Line Depreciation Rate - Solar |  |  |  | 20
6 | SFD = R/((1+R)^n-1) (sinking fund) - Solar | G11/((1+G11)^(F5)-1) |  |  |  | 2.373%
7
8 |  |  | % | Rate | Wtd. Rate
9 | Debt | PJM TO Generic Value | 50% | 4% | 2%
10 | Equity | PJM TO Generic Value | 50% | 10.5% | 5.25%
11 | Total |  | 100% |  | 7.25% | 7.25%
12
13 | Total Fixed Charge Carrying Rate - Solar | G2+G6+G11 |  |  |  | 11.62%
14
15 | Fixed Operating Expenses Rate - Wind | EPC Estimate - OpEx / CapEx |  |  |  | 3%
16
17 | Depreciation Expense Rate (SLD=1/n) - Wind | 1/F18 | 4%
18 | 1 / Straight-Line Depreciation Rate - Wind |  |  |  | 25
19 | SFD = R/((1+R)^n-1) (sinking fund) - Wind | G24/((1+G24)^(F18)-1) |  |  |  | 1.525%
20
21 |  |  | % | Rate | Wtd. Rate
22 | Debt | PJM TO Generic Value | 50% | 4% | 2%
23 | Equity | PJM TO Generic Value | 50% | 10.5% | 5.25%
24 | Total |  | 100% |  | 7.25% | 7.25%
25
26 | Total Fixed Charge Carrying Rate - Wind | G15+G19+G24 |  |  |  | 11.78%