## GenDeliv(Summer)
2024 RTEP Preliminary
PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | kVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Comment
533 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 232.9 | 229.2 | 142.02 | 139.75 | DVP_P7-1: LN 2058-2181 | Tower | Tie Line to Non PJM facility. Dominion summer emergency rating is 219 MVA. DEP summer emergency rating is 164 MVA.
538 | 231215 | SILVERSD | 231205 | DARLEY | 1 | 69 | 235 | 175 | 203.6 | 196.8 | 116.36 | 112.44 | DPL_P7_1_DBL_5NC | Tower
539 | 231205 | DARLEY | 231211 | NAAMANS | 1 | 69 | 235 | 136 | 147.9 | 144.4 | 108.78 | 106.2 | DPL_P7_1_DBL_5NC | Tower
7 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 719.1 | 773.2 | 761.7 | 107.53 | 105.92 | DVP_P1-2: LN 274 | Single
540 | 243026 | 05KAMMER13 | 243012 | 05G WASHGTN1 | 1 | 138 | 205 | 621 | 658.8 | 651.7 | 106.09 | 104.95 | AEP_P7-1_#11151 | Tower
321 | 214062 | WSTMLNDE | 213873 | PENCOYD2 | 1 | 69 | 230 | 103 | 101.1 | 107.6 | 98.16 | 104.45 | PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK | Breaker
322 | 213786 | MASTER 2 | 214062 | WSTMLNDE | 1 | 69 | 230 | 103 | 101.1 | 107.6 | 98.19 | 104.43 | PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK | Breaker
496 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-2-PE-138-021B | Bus | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
326 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-3-PE-138-008A_A | Breaker | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
327 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-3-PE-138-009A_A | Breaker | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
329 | 235707 | 01WYLIE R | 235710 | 01WYLIE R | 3 | 345/138 | 201 | 515 | 525.8 | 531.7 | 102.09 | 103.24 | AP-P2-3-MP-138-210T | Breaker
330 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 197.1 | 196.1 | 103.76 | 103.23 | ATSI-P2-3-TE-138-010C | Breaker | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
331 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 194.6 | 194.5 | 102.43 | 102.37 | ATSI-P2-3-TE-138-009 | Breaker | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
497 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 194.6 | 194.5 | 102.43 | 102.37 | ATSI-P2-2-TE-138-004 | Bus | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
544 | 238581 | 02BRBRTN | 239619 | 02ALCOA | 1 | 138 | 202 | 282 | 277.2 | 284.9 | 98.3 | 101.01 | ATSI-P7-1-OEC-345-003 | Tower
337 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-3-PE-138-009A_A | Breaker | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
338 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-3-PE-138-008A_A | Breaker | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
500 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-2-PE-138-021B | Bus | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
12 | 243026 | 05KAMMER13 | 243012 | 05G WASHGTN1 | 1 | 138 | 205 | 446 | 455.9 | 449.5 | 102.21 | 100.78 | Base Case | Single
Note
The circuit is mostly limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
The loading on column 'M' is due to contribution from suspended generators and the loading on the circuit should be <100% without those suspended generators.

## N-1 Thermal (Summer)
2023 RTEP Preliminary
PJM N-1 Thermal Result (Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Comment
54 | 214062 | WSTMLNDE | 213873 | PENCOYD2 | 1 | 69/69 | 230/230 | 103 | 98.1553 | 104.45 | Line_FB | 'PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK'
55 | 213786 | MASTER 2 | 214062 | WSTMLNDE | 1 | 69/69 | 230/230 | 103 | 98.1553 | 104.43 | Line_FB | 'PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK'