## Types
Data from PJM to Member
B1Name | B2Name | B3Name | Element | Notes | Analog/Digital | Source | Comment
STATION | VOLTAGE | UNIT | GENECON | Economic Base Point | Analog | Markets
STATION | VOLTAGE | UNIT | GENMAXEN | Economic Max Limit | Analog | Markets
STATION | VOLTAGE | UNIT | GENMINEN | Economic Min Limit | Analog | Markets
STATION | VOLTAGE | UNIT | MAXEMCAP | Emergency Max Limit | Analog | Markets
STATION | VOLTAGE | UNIT | HIMRLIM | High MVAR Limit | Analog | TNA
STATION | VOLTAGE | UNIT | LOMRLIM | Low MVAR Limit | Analog | TNA
STATION | VOLTAGE | UNIT | AREG | Assigned Regulation A | Analog | Markets | Reg Market Only - Unit and/or DSR
STATION | VOLTAGE | UNIT | AREGD | Assigned Regulation D | Analog | Markets | Reg Market Only - Unit and/or DSR
STATION | VOLTAGE | UNIT | ASPIN | Assigned Spin Reserves | Analog | Markets | Reserves - Unit and/or DSR
STATION | VOLTAGE | UNIT | NSRSPIN | Assigned Non-Synchronized Spin Reserves | Analog | Markets | Reserves - Unit and/or DSR
STATION | VOLTAGE | UNIT | ASECRES | Assigned Secondary Reserve | Analog | Markets | Reserves - Unit and/or DSR
STATION | VOLTAGE | UNIT | GENRUNR | Unit Dispatch Mode | Analog | Markets | Unit Dispatch Mode (0-36)
STATION | VOLTAGE | UNIT | CURTAIL | Curtailment Flag | Analog | Markets | Curtail Flag. Wind Farms only. 1 = Curtail, 2 = No Curtail
STATION | VOLTAGE | UNIT | ACNREAS | Auto CT Callon Reason | Analog | Markets | CTs only - Auto CT Callon Reason (2 to 36)
STATION | VOLTAGE | UNIT | ACNTIME | Auto CT Callon time | Analog | Markets | CTs only - Auto CT Callon Time (Day*10,000 + Hour*100 + Minute)
STATION | VOLTAGE | UNIT | KVSCHED | Voltage Schedule | Analog | TO
STATION | VOLTAGE | UNIT | CPEVENT | Performance Assessment Interval Indicator | Analog | Markets | PAI Event (0 = Invalid, 1 = PAI Event, 2 = no PAI Event, 3 = PAI Drill)
REGZONE | FLEET | GENA | REGA | Fleet Regulation A Control signal | Analog | AGC | Reg Market Only - Unit and/or DSR
REGZONE | FLEET | GEND | REGD | Fleet Regulation D Control signal | Analog | AGC | Reg Market Only - Unit and/or DSR
PJMC | SPIN | PJM RTO | CB | RTO Spin Event | Digital | Markets or Operator | SCADA (1 = Deactivated, 0 = Activated), ICCP Object ID PJMPJMCSPINPJMRTOCB (2 = Deactivated, 1 = Activated)
PJMC | SPIN | PJM | CB | Zonal Spin Event | Digital | Markets or Operator | SCADA (1 = Deactivated, 0 = Activated), ICCP Object ID PJMPJMCSPINPJMCB (2 = Deactivated, 1 = Activated)
PJMC | SPIN | TEST | CB | Test Spin Event | Digital | Operator | SCADA (1 = Deactivated, 0 = Activated), ICCP Object ID PJMPJMCSPINTESTCB (2 = Deactivated, 1 = Activated)
Data from Member to PJM
B1Name | B2Name | B3Name | Element | Notes | Analog/Digital | Source | Comment
STATION | VOLTAGE | UNIT | GENMR | Unit Gross MVAR Output | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | GENMW | Unit Gross MW Output | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | KV | Unit Low side voltage | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | MR | Unit Aux Load MVAR | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | MW | Unit Aux Load MW | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | HI MR | Unit High side Net MVAR | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | HI MW | Unit High side Net MW | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | CB | Unit Low side CB | Digital | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | CB | Unit High side GSU CB | Digital | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | BUS | KV | High side bus voltage | Analog | Member | Data for Network Model - dependent on how unit is modeled
LINE | VOLTAGE | GENLEAD | ENDB MR | Gen Lead Line MVAR output (Total Net MVAR) | Analog | Member | Data for Network Model - dependent on how unit is modeled
LINE | VOLTAGE | GENLEAD | ENDB MW | Gen Lead Line MW output (Total Net MW) | Analog | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | LINECB | CB | Line Breaker | Digital | Member | Data for Network Model - dependent on how unit is modeled
STATION | VOLTAGE | UNIT | NETMW | Unit Net MW Output | Analog | Member
STATION | VOLTAGE | UNIT | AVR | Unit Automatic Voltage Regulator | Digital | Member
STATION | VOLTAGE | UNIT | PSS | Unit Power System Stabilizer | Digital | Member
STATION | VOLTAGE | UNIT | SECRESST | Reserve Availability Status | Digital | Member | Reserves - SCADA (1 = Available, 0 = Unavailable), ICCP (2 = Available, 1 = Unavailable)
REGZONE | FLEET | GENA | CREG | Fleet Regulation A Capacity | Analog | Member | Reg Market Only - Unit and/or DSR
REGZONE | FLEET | GEND | CREG | Fleet Regulation D Capacity | Analog | Member | Reg Market Only - Unit and/or DSR
REGZONE | FLEET | GENA | TREG | Fleet Regulation A Contribution | Analog | Member | Reg Market Only - Unit and/or DSR
REGZONE | FLEET | GEND | TREG | Fleet Regulation D Contribution | Analog | Member | Reg Market Only - Unit and/or DSR
STATION | VOLTAGE | UNIT | LOADBP | Total Load Basepoint | Analog | Member | Unit or DSR
STATION | VOLTAGE | UNIT | WBPRES | Barometric Pressure | Analog | Member | Wind Farms only
STATION | VOLTAGE | UNIT | WHUMID | Humidity | Analog | Member | Wind Farms only
STATION | VOLTAGE | UNIT | WTEMPF | Temperature (Fahrenheit) | Analog | Member | Wind Farms and Solar only
STATION | VOLTAGE | UNIT | WWDIR | Wind Direction | Analog | Member | Wind Farms and Solar only
STATION | VOLTAGE | UNIT | WWSPD | Wind Speed | Analog | Member | Wind Farms and Solar only
STATION | VOLTAGE | SP | SLRIRD | Solar Irradiance (W/m^2) | Analog | Member | Solar only
STATION | VOLTAGE | SP | BPTEMP | Back Panel Temperature (Fahrenheit) | Analog | Member | Solar only
STATION | VOLTAGE | HYD 1 | PONDLEV | Pond Level | Analog | Member | Hydros only
STATION | VOLTAGE | UNIT | ACNACK | Auto CT Callon Acknowledgement | Analog | Member | CTs only